## MDB-1
OA No. | Technical Room (Signal Location 2) | Design Area | Tag Number | TagNumber | Old Tag Number | Instrument Type | Instrument Type Description | Process Function Type | Loop Name | Internal Loop Order | P&ID | Service | Tag Service 1 and 2 | Equipment Name | Equipment Description | WBS | Status | Typical_No | Package Number | Location | System 1 (System) | System 2 | I/O Type Name | I/O Type Name 2 | Signal Type | Execution | External Power Supply | Signal Level | Loop Powered | Voting | Asset | Contact Type | Junction Box / Panel | Multi-cable / Cable | Multipair Cable No. | Pair Number | IO Grouping | Logic Number | Point Type | Machine Level | Equipment Type | Monitoring Frequency Of Interest (Hz) (MPS) | Measurement Evaluation | Transducer Orientation (MPS) | Probe Freq range Min (MPS) | Probe Freq range Max (MPS) | Probe Sensitivity (MPS) | Probe Model / Part Number | Probe Extension Cable length | Measuring Unit (include the below units into existing list) | Key Phasor Measurement | System Tag Name | Controller type | Controller Assignment | System Cabinet Name | Marshalling Cabinet Name | Marshalling Cabinet T.B No | TB 1 | TB 2 | TB 3 | FTA Name | FTA Cable Name | I/O Allocation CIOC/CSLS | Charm Baseplate | Charm Slot | Manufacturer Name | Model Name | Discrete Invert | 1 State Word | 0 State Word | Discrete Alarm Priority | Discrete Alarm Enable | Analog Range Low Scale | Analog Range High Scale | Analog Range EU | Min Transmitter Calibration Range | Max Transmitter Calibration Range | Transmitter Scale Units | High High High Alarm | High High High Alarm Limit | High High High Alarm Priority | High High Alarm | High High Alarm Limit | High High Alarm Priority | High Alarm | High Alarm Limit | High Alarm Priority | Low Alarm | Low Alarm Limit | Low Alarm Priority | Low Low Alarm | Low Low Alarm Limit | Low Low Alarm Priority | Low Low Low Alarm | Low Low Low Alarm Limit | Low Low Low Alarm Priority | Alarm Deadband | Square Root | Low Cutoff Value | Module Scan Rate | Main Display | Friendly Name | Parent | Loop Reference 1 | Loop Reference 2 | I/O Allocation EIOC | I/O Allocation Physical Device Name | I/O Allocation Logical Device Name | I/O Allocation Register Name | SP Track PV in MAN | SP Low Range | SP High Range | PID Control Direction | P Action | I Action | D Action | Master-Slave Reference | Valve Action | Allowable Valve Travel Time | Revision # | Revision Change Type | Revision Comments | Revision Date | Alarm_Set_Point | Alarm_Priority | IRP_Cabinet_Name | Feed_Name | Feed_From | Feed_TS_Name | Feed_TS_Term | Ele_Cable_name | Ele_Cable_Type | Ele_Cable_Term | Ele_TS_Name | Ele_TS_Term | Relay_Name | Relay_Model | Relay_Contact | Relay_Term_Coil | Relay_Term_Contact | SYS_TS_Name | SYS_TS_Term
OA-11 | PIB-30 | RA 320-01 | 320-FT -20645-A | 320FT20645A | - | FT | dP Flow Transmitter | Flow | 320-F -20645 | 30 | PID-320200601 | LPN TO 320-F-2011 ETHYLENE TREATER REGENERATION HEATER | LPN TO F-2011 ETH HTR | - |  | 320 | New | - | - | L | DCS | - | ai | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 1 | A-CONTROL | 320-UC-20060 | [13 empty] | 320FT20645A | [15 empty] | - | - | - | - | - | 0 | 9 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | N | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -20645 | 320FV20645 | - | FV | Control Valve | Control Valve | 320-F -20645 | 80 | PID-320200601 | LPN TO 320-F-2011 ETHYLENE TREATER REGENERATION HEATER | LPN TO F-2011 ETH HTR | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 2 | A | - | [13 empty] | 320FV20645 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -80002 | 320FT80002 | - | FT | dP Flow Transmitter | Flow | 320-F -80002 | 30 | PID-320800001 | CWS TO K-8061-A/B | CWS TO K-8061-A/B | - |  | 320 | DELETED | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 3 | - | - | [13 empty] | 320FT80002 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | N | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | Tag deleted. | 2024-11-15 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -80004 | 320FT80004 | - | FT | dP Flow Transmitter | Flow | 320-F -80004 | 30 | PID-320800001 | 320-K-8061A/B HP NITROGEN COMPRESSOR SUCTION | K-8061A/B HPN CMPR SUCT | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 4 | - | - | [13 empty] | 320FT80004 | [15 empty] | - | - | - | - | - | 0 | 680 | kg/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | N | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -80001 | 320LT80001 | - | LT | dP Level Transmitter | Level | 320-L -80001 | 40 | PID-320800001 | 320-D-8060 HP NITROGEN SURGE SUCTION DRUM | D-8060 HPN SRG SUCT DRM | 320-D-8060 | HP NITROGEN SURGE SUCTION DRUM | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 4 | - | - | [13 empty] | 320LT80001 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -80002 | 320LT80002 | - | LT | dP Level Transmitter | Level | 320-L -80002 | 40 | PID-320800001 | 320-D-8061 HP N ITROGEN DISCHARGE DRUM | D-8061 HPN DISCH DRM | 320-D-8061 | HP N ITROGEN DISCHARGE DRUM | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 6 | - | - | [13 empty] | 320LT80002 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -81209 | 320LT81209 | - | LT | dP Level Transmitter | Level | 320-L -81209 | 40 | PID-320801201 | 320-D-8064 POTABLE WATER VESSEL | D-8064 PWA VESL | 320-D-8064 | POTABLE WATER VESSEL | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 7 | A-CONTROL | - | [13 empty] | 320LT81209 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -83050 | 320LT83050 | - | LT | dP Level Transmitter with seal | Level | 320-L -83050 | 0 | PID-320803005 | 320-D-8069 SUSPECT CONDENSATE KNOCK OUT DRUM | D-8069 SSC KOD | 320-D-8069 | SUSPECT CONDENSATE KO DRUM | 320 | New | - | - | L | DCS | - | XQ | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 8 | A-CONTROL | - | [13 empty] | 320LT83050 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -80002 | 320PT80002 | - | PT | Pressure Transmitter | Pressure | 320-P -80002 | 30 | PID-320800001 | PLANT UNIT 1 LPN FROM OSBL | PLANT UNIT 1 LPN FRM OSBL | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 9 | - | - | [13 empty] | 320PT80002 | [15 empty] | - | - | - | - | - | 0 | 15 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -80016-A | 320PT80016A | - | PT | Pressure Transmitter | Pressure | 320-P -80016 | 30 | PID-320800001 | 320-K-8061A/B HP NITROGEN COMPRESSOR DISCHARGE | K-8061A/B HPN CMPR DISCH | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 10 | - | 320-UC-80001 | [13 empty] | 320PT80016A | [15 empty] | - | - | - | - | - | 0 | 80 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -80016-B | 320PT80016B | - | PT | Pressure Transmitter | Pressure | 320-P -80016 | 31 | PID-320800001 | 320-K-8061A/B HP NITROGEN COMPRESSOR DISCHARGE | K-8061A/B HPN CMPR DISCH | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 11 | - | 320-UC-80001 | [13 empty] | 320PT80016B | [15 empty] | - | - | - | - | - | 0 | 80 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -80017 | 320PT80017 | - | PT | Pressure Transmitter | Pressure | 320-P -80017 | 30 | PID-320800001 | 320-K-8061A/B HP NITROGEN DISCHARGE | K-8061-A/B HPN DISCH | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 12 | - | - | [13 empty] | 320PT80017 | [15 empty] | - | - | - | - | - | 0 | 75 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PV -80017-A | 320PV80017A | 320-PV -80017 | PV | Control Valve | Control Valve | 320-P -80017 | 80 | PID-320800001 | 320-K-8061A/B HP NITROGEN DISCHARGE | K-8061-A/B HPN DISCH | - |  | 320 | Modified | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 13 | - | - | [13 empty] | 320PV80017A | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | FC |  | 05A | PDR-1 | Tag Renamed | [8 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PDT -80018 | 320PDT80018 | - | PDT | Diff.Pressure Transmitter | Pressure | 320-PD-80018 | 30 | PID-320800001 | PLANT UNIT 1 LPN FROM OSBL | PLANT UNIT 1 LPN FRM OSBL | - |  | 320 | New | - | - | L | DCS | - |  | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 14 | - | - | [13 empty] | 320PDT80018 | [15 empty] | - | - | - | - | - | 0 | 1 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -80003 | 320TT80003 | - | TT | Temperature Transmitter | Temperature | 320-T -80003 | 30 | PID-320800001 | PLANT UNIT 1 LPN FROM OSBL | PLANT UNIT 1 LPN FRM OSBL | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 15 | - | - | [13 empty] | 320TT80003 | [15 empty] | - | - | - | - | - | 0 | 60 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -80005 | 320TT80005 | - | TT | Temperature Transmitter | Temperature | 320-T -80005 | 30 | PID-320800001 | 320-K-8061A/B CWR | K-8061-A/B CWR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 16 | - | - | [13 empty] | 320TT80005 | [15 empty] | - | - | - | - | - | 0 | 70 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -83004 | 320TT83004 | - | TT | Temperature Transmitter | Temperature | 320-T -83004 | 0 | PID-320803002 | 320-A-8063 VENT STEAM CONDENSER INLET | A-8063 VENT STM COND IN | - |  | 320 | Modified | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 18 | - | - | [13 empty] | 320TT83004 | [15 empty] | - | - | - | - | - | 0 | 150 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range Updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -83013-AO | 320XLS83013AO | - | XLS | Position Limit Switch | General | 320-X -83013 | 31 | PID-320803003 | 320-G-8062-B CLEAN CONDENSATE SUCTION | G-8062-B CLN CNDS SUCT | - |  | 320 | Modified | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 19 | - | 320-UC-83061 | [13 empty] | 320XLS83013AO | [15 empty] | F | D-8062 | D-8069 | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -83013-BO | 320XLS83013BO | - | XLS | Position Limit Switch | General | 320-X -83013 | 31 | PID-320803003 | 320-G-8062-B SUSPECT CONDENSATE SUCTION | G-8062-B SSC SUCT | - |  | 320 | Modified | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0001 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0001 | Pair 20 | - | 320-UC-83061 | [13 empty] | 320XLS83013BO | [15 empty] | F | D-8069 | D-8062 | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -83010 | 320FT83010 | - | FT | dP Flow Transmitter | Flow | 320-F -83010 | 30 | PID-320803003 | 320-G-8062-A/B CLEAN CONDENSATE OUTLET | G-8062-A/B CLN CNDS OUT | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 1 | - | - | [13 empty] | 320FT83010 | [15 empty] | - | - | - | - | - | 0 | 31 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | N | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -83005 | 320LT83005 | - | LT | dP Level Transmitter with seal | Level | 320-L -83005 | 0 | PID-320803002 | 320-D-8062 CONDENSATE KNOCK OUT DRUM | D-8062 CNDS KOD | 320-D-8062 | CONDENSATE KNOCK OUT DRUM | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 2 | B | - | [13 empty] | 320LT83005 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LV -83006 | 320LV83006 | - | LV | Control Valve | Control Valve | 320-L -83006 | 0 | PID-320803001 | 320-D-8068 MP CONDENSATE KO DRUM | D-8068 MP CNDS KO DRM | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 3 | - | - | [13 empty] | 320LV83006 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -83008 | 320LT83008 | - | LT | dP Level Transmitter with seal | Level | 320-L -83008 | 0 | PID-320803001 | 320-D-8068 MP CONDENSATE KO DRUM | D-8068 MP CNDS KO DRM | 320-D-8068 | MP CONDENSATE K.O DRUM | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 |  | B-ALARM | - | [13 empty] | 320LT83008 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -20142-B | 320PT20142B | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -20142 | 31 | PID-320200103 | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | D-2020 H2 TO R-4101/4201 | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 5 | B | 320-UC-20011 | [13 empty] | 320PT20142B | [15 empty] | - | - | - | - | - | 0 | 90 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -20143-B | 320PT20143B | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -20143 | 31 | PID-320200103 | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | D-2020 H2 TO R-4101/4201 | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 6 | - | - | [13 empty] | 320PT20143B | [15 empty] | - | - | - | - | - | 0 | 65 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PV -20143-B | 320PV20143B | - | PV | Control Valve | Control Valve | 320-P -20143 | 81 | PID-320200103 | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | D-2020 H2 TO R-4101/4201 | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 7 | B | - | [13 empty] | 320PV20143B | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PV -20648 | 320PV20648 | - | PV | Control Valve | Control Valve | 320-P -20648 | 80 | PID-320200601 | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | REG RTRN TO A-2062 | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 8 | - | - | [13 empty] | 320PV20648 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FO |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -20657 | 320PT20657 | - | PT | Pressure Transmitter | Pressure | 320-P -20657 | 30 | PID-320200601 | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | REG RTRN TO A-2062 | - |  | 320 | New | - | 320-F-2011 | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 9 | B-ALARM | - | [13 empty] | 320PT20657 | [15 empty] | - | - | - | - | - | 0 | 3 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -83001 | 320PT83001 | - | PT | Pressure Transmitter | Pressure | 320-P -83001 | 30 | PID-320803002 | 320-D-8062 CONDENSATE KNOCK OUT DRUM | D-8062 CNDS KOD | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 10 | - | - | [13 empty] | 320PT83001 | [15 empty] | - | - | - | - | - | 0 | 0.1 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -83008 | 320PT83008 | - | PT | Pressure Transmitter | Pressure | 320-P -83008 | 0 | PID-320803004 | 320-G-8068-B MP CONDENSATE PUMP DIAPHRAGM FAILURE | G-8068-B DIAPHRAGM FAIL | 320-G-8068-B |  | 320 | New | - | PKG-034001 | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 99 | B | - | [13 empty] | 320PT83008 | [15 empty] | - | - | - | - | - | 0 | 30 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20488 | 320TT20488 | - | TT | Temperature Transmitter | Temperature | 320-T -20488 | 30 | PID-320200401 | ETHYLENE FROM 320-E-2002 HEATER TO FLARE | E-2002 ETH TO FLR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 12 | - | - | [13 empty] | 320TT20488 | [15 empty] | - | - | - | - | - | -110 | 180 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20660 | 320TT20660 | - | TT | Temperature Transmitter | Temperature | 320-T -20660 | 30 | PID-320200601 | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | REG RTRN TO A-2062 | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 13 | - | - | [13 empty] | 320TT20660 | [15 empty] | - | - | - | - | - | -110 | 420 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20662 | 320TT20662 | - | TT | Temperature Transmitter | Temperature | 320-T -20662 | 30 | PID-320200601 | REGEN RETURN AND COOLING NITROGEN RETURN TO FLARE FROM 320-A-2062 VENT COOLER | A-2062 REG RTRN TO FLR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 14 | - | - | [13 empty] | 320TT20662 | [15 empty] | - | - | - | - | - | -110 | 200 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -83007 | 320TT83007 | - | TT | Temperature Transmitter | Temperature | 320-T -83007 | 0 | PID-320803002 | 320-A-8063 VENT STEAM CONDENSER OUTLET | A-8063 VENT STM COND OUT | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 15 | - | - | [13 empty] | 320TT83007 | [15 empty] | - | - | - | - | - | 0 | 150 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -83052 | 320TT83052 | - | TT | Temperature Transmitter | Temperature | 320-T -83052 | 0 | PID-320803005 | 320-A-8064 SUSPECT VENT STEAM CONDENSER OUTLET | A-8064 SS STM COND OUT | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | 16 | - | - | [13 empty] | 320TT83052 | [15 empty] | - | - | - | - | - | 0 | 150 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -83011-C | 320XLS83011C | - | XLS | Position Limit Switch | General | 320-X -83011 | 30 | PID-320803003 | 320-G-8062-B CLEAN CONDENSATE TO 320-D-8062 | G-8062-B CLN CNDS/D-8062 | - |  | 320 | Modified | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 17 | - | 320-UC-83061 | [13 empty] | 320XLS83011C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -83011-O | 320XLS83011O | - | XLS | Position Limit Switch | General | 320-X -83011 | 31 | PID-320803003 | 320-G-8062-B CLEAN CONDENSATE TO 320-D-8062 | G-8062-B CLN CNDS/D-8062 | - |  | 320 | Modified | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 18 | - | 320-UC-83061 | [13 empty] | 320XLS83011O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PDT -86352 | 320PDT86352 | 320-FT -20646-B | PDT | Diff. Pressure Transmitter with Seal | Pressure | 320-PD-86352 | 30 | PID-320806303 | D-8002 FLR TO G-8002-B | D-8002 FLR TO G-8002-B | - |  | 320 | Modified | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0004 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0004 | Pair 19 | B | - | [13 empty] | 320PDT86352 | [15 empty] | - | - | - | - | - | 0 | 0.1 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42766 | 320FT42766 | - | FT | dP Flow Transmitter | Flow | 320-F -42766 | 30 | PID-320402701 | 320-G-4202 COOLANT SUPPLY TO 320-E-4201A/B/C EXCHANGER | G-4202 CLNT/E-4201A/B/C | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0035 | 06PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0035 | Pair 1 | - | - | [13 empty] | 320FT42766 | [15 empty] | - | - | - | - | - | 0 | 4660 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | N | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -41752-A | 320TT41752A | - | TT | Temperature Transmitter | Temperature | 320-T -41752 | 30 | PID-320401702 | COOLANT SUPPLY TO 320-R-4101 REACTOR A | CLNT SPLY TO R-4101 | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0035 | 06PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0035 | Pair 2 | - | - | [13 empty] | 320TT41752A | [15 empty] | - | - | - | - | - | 0 | 120 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -42753-A | 320TT42753A | - | TT | Temperature Transmitter | Temperature | 320-T -42753 | 30 | PID-320402702 | COOLANT SUPPLY TO 320-R-4201 REACTOR B | CLNT SPLY TO R-4201 | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0035 | 06PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0035 | Pair 3 | - | - | [13 empty] | 320TT42753A | [15 empty] | - | - | - | - | - | 0 | 120 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -82118 | 320TT82118 | - | TT | Temperature Transmitter | Temperature | 320-T -82118 | 0 | PID-320802101 | 320-DS-8211 MPS DESUPERHEATER VENT TO ATM | DS-8211 MPS VENT TO ATM | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0035 | 06PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0035 | Pair 4 | A | - | [13 empty] | 320TT82118 | [15 empty] | - | - | - | - | - | -25 | 150 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -20363 | 320LT20363 | - | LT | dP Level Transmitter with seal | Level | 320-L -20363 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER | D-2034-A HXE TRT | 320-D-2034-A | HEXENE TREATER | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | PAIR 1 | A | - | [13 empty] | 320LT20363 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -20245 | 320PT20245 | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -20245 |  | PID-320200201 | LPN TO 320-D-2032 HEXENE SURGE TANK | LPN TO D-2032 HXE SRG TK | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 2 | - | - | [13 empty] | 320PT20245 | [15 empty] | - | - | - | - | - | 0 | 3 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -20301 | 320PT20301 | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -20301 | 30 | PID-320200301 | HEXENE FROM 320-E-5043 SIDEDRAW CONDENSER TO 320-D-2034-A/B | E-5043 HXE TO D-2034-A/B | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 3 | A | - | [13 empty] | 320PT20301 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20350 | 320TT20350 | - | TT | Temperature Transmitter | Temperature | 320-T -20350 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER | D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 4 | A | 320-UC-20061 | [13 empty] | 320TT20350 | [15 empty] | - | - | - | - | - | 0 | 350 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20351 | 320TT20351 | - | TT | Temperature Transmitter | Temperature | 320-T -20351 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER | D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 5 | A | 320-UC-20061 | [13 empty] | 320TT20351 | [15 empty] | - | - | - | - | - | 0 | 350 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 |  | 320-TT -20361 | 320TT20361 | - | TT | Temperature Transmitter | Temperature | 320-T -20361 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER OUTLET | D-2034-A HXE TRT OUT | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 6 | A | - | [13 empty] | 320TT20361 | [15 empty] | - | - | - | - | - | 0 | 70 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20362 | 320TT20362 | - | TT | Temperature Transmitter | Temperature | 320-T -20362 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER | D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 7 | A | 320-UC-20061 | [13 empty] | 320TT20362 | [15 empty] | - | - | - | - | - | 0 | 350 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20365 | 320TT20365 | - | TT | Temperature Transmitter | Temperature | 320-T -20365 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER BOTTOM | D-2034-A HXE TRT BTM | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 8 | A | 320-UC-20061 | [13 empty] | 320TT20365 | [15 empty] | - | - | - | - | - | 0 | 350 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20388 | 320TT20388 | - | TT | Temperature Transmitter | Temperature | 320-T -20388 | 30 | PID-320200301 | 320-D-2034-A HEXENE TREATER | D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 9 | A | 320-UC-20061 | [13 empty] | 320TT20388 | [15 empty] | - | - | - | - | - | 0 | 350 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20301-C | 320XLS20301C | - | XLS | Position Limit Switch | General | 320-X -20301 | 30 | PID-320200301 | LOW PRESSURE NITROGEN TO 320-D-2034-A HEXENE TREATER | LPN TO D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 10 | A | 320-UC-20061 | [13 empty] | 320XLS20301C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20301-O | 320XLS20301O | - | XLS | Position Limit Switch | General | 320-X -20301 | 31 | PID-320200301 | LOW PRESSURE NITROGEN TO 320-D-2034-A HEXENE TREATER | LPN TO D-2034-A HXE TRT | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 11 | A | 320-UC-20061 | [13 empty] | 320XLS20301O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20302-C | 320XLS20302C | - | XLS | Position Limit Switch | General | 320-X -20302 | 30 | PID-320200301 | REGEN SUPPLY & COOLING NITROGEN SUPPLY TO 320-D-2034-A HEXEN TREATER | REG & CLG N2 TO D-2034-A | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 12 | A | 320-UC-20061 | [13 empty] | 320XLS20302C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20302-O | 320XLS20302O | - | XLS | Position Limit Switch | General | 320-X -20302 | 31 | PID-320200301 | REGEN SUPPLY & COOLING NITROGEN SUPPLY TO 320-D-2034-A HEXEN TREATER | REG & CLG N2 TO D-2034-A | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 13 | A | 320-UC-20061 | [13 empty] | 320XLS20302O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20305-C | 320XLS20305C | - | XLS | Position Limit Switch | General | 320-X -20305 | 30 | PID-320200301 | 320-D-2034-A REGEN RETURN & COOLING NITROGEN RETURN TO FLARE HEADER | D-2034A REG RTRN TO FLR | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 14 | A | 320-UC-20061 | [13 empty] | 320XLS20305C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20305-O | 320XLS20305O | - | XLS | Position Limit Switch | General | 320-X -20305 | 31 | PID-320200301 | 320-D-2034-A REGEN RETURN & COOLING NITROGEN RETURN TO FLARE HEADER | D-2034A REG RTRN TO FLR | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 15 | A | 320-UC-20061 | [13 empty] | 320XLS20305O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20306-C | 320XLS20306C | - | XLS | Position Limit Switch | General | 320-X -20306 | 30 | PID-320200301 | HEXENE TO 320-D-2032 HEXENE SURGE VESSEL | HXE TO D-2032 SRG VESL | - |  | 320 | deleted | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 16 | A | 320-UC-20061 | [13 empty] | 320XLS20306C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20306-O | 320XLS20306O | - | XLS | Position Limit Switch | General | 320-X -20306 | 31 | PID-320200301 | HEXENE TO 320-D-2032 HEXENE SURGE VESSEL | HXE TO D-2032 SRG VESL | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 17 | A | 320-UC-20061 | [13 empty] | 320XLS20306O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20309-C | 320XLS20309C | - | XLS | Position Limit Switch | General | 320-X -20309 | 30 | PID-320200301 | HEXENE TO 320-S-2034 HEXENE FILTER FROM 320-D-2034-A | D-2034-A HXE TO S-2034 | - |  | 320 | New | HEXENE TO 320-S-2034 HEXENE FILTER | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 18 | A | 320-UC-20061 | [13 empty] | 320XLS20309C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20309-O | 320XLS20309O | - | XLS | Position Limit Switch | General | 320-X -20309 | 31 | PID-320200301 | HEXENE TO 320-S-2034 HEXENE FILTER FROM 320-D-2034-A | D-2034-A HXE TO S-2034 | - |  | 320 | New | HEXENE TO 320-S-2034 HEXENE FILTER | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0040 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0040 | Pair 19 | A | 320-UC-20061 | [13 empty] | 320XLS20309O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -20205 | 320TT20205 | - | TT | Temperature Transmitter | Temperature | 320-T -20205 | 30 | PID-320200202 | HEXENE FROM 320-G-2032-B DISCHARGE TO 320-E-2033 HEXENE COOLER | G-2032B HXE / E-2033 CLR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 1 | - | - | [13 empty] | 320TT20205 | [15 empty] | - | - | - | - | - | 0 | 70 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Wiring updated to avoid cross-controller communication as per Emerson suggestion. Range updated. | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-LT -20371 | 320LT20371 | - | LT | dP Level Transmitter with seal | Level | 320-L -20371 | 30 | PID-320200302 | 320-D-2034-B HEXENE TRAETER | D-2034-B HXE TRAETER | 320-D-2034-B | HEXENE TREATER | 320 |  | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 3 | B | - | [13 empty] | 320LT20371 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -40211-A | 320PT40211A | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -40211 | 30 | PID-320400202 | REGEN SPLY TO 320-D-4143-B RECYCLE ISOBUTANE TREATER INLET/OUTLET | REG SPLY TO D-4143-B | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 4 | B | - | [13 empty] | 320PT40211A | [15 empty] | - | - | - | - | - | 0 | 30 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -40211-B | 320PT40211B | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -40211 | 31 | PID-320400202 | REGEN SPLY TO 320-D-4143-B RECYCLE ISOBUTANE TREATER INLET/OUTLET | REG SPLY TO D-4143-B | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 5 | B | - | [13 empty] | 320PT40211B | [15 empty] | - | - | - | - | - | 0 | 30 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PDT -40227 | 320PDT40227 | - | PDT | Diff.Pressure Transmitter with Seal | Pressure | 320-PD-40227 | 30 | PID-320400203 | 320-4243 RECYCLE ISOBTANE FILTER PRESSURE | S-4243 RCYCL IBT FLTR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 6 | - | - | [13 empty] | 320PDT40227 | [15 empty] | - | - | - | - | - | 0 | 1 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XHSC -20202-L | 320XHSC20202L | - | XHSC | Hand Switch | General | 320-X -20202 |  | PID-320200202 | HEXENE FROM 320-G-2032-B DISCHARGE | HXE FRM G-2032-B DISCH | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 7 | B | 320-UC-20070 | [13 empty] | 320XHSC20202L | [15 empty] | F | CLOSE | NO ACTION | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XHSO -20202-L | 320XHSO20202L | - | XHSO | Hand Switch | General | 320-X -20202 |  | PID-320200202 | Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ Servicio ñandú é — 温度 °C ✓ | HXE FRM G-2032-B DISCH | - |  | 320 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 8 | B | 320-UC-20070 | [13 empty] | 320XHSO20202L | [15 empty] | F | OPEN | NO ACTION | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20202-C | 320XLS20202C | - | XLS | Position Limit Switch | General | 320-X -20202 | 30 | PID-320200202 | HEXENE FROM 320-G-2032-B DISCHARGE | HXE FRM G-2032-B DISCH | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DI | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 9 | B | - | [13 empty] | 320XLS20202C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -20202-O | 320XLS20202O | - | XLS | Position Limit Switch | General | 320-X -20202 | 31 | PID-320200202 | HEXENE FROM 320-G-2032-B DISCHARGE | HXE FRM G-2032-B DISCH | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DI | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0045 | 12PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0045 | Pair 10 | B | - | [13 empty] | 320XLS20202O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -42420 | 320FV42420 | - | FV | Control Valve | Control Valve | 320-F -42420 | 80 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201 LOOP REACTOR B LEG .8 | RIB FLUSH TO R-4201 L8 | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 1 | - | - | [13 empty] | 320FV42420 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | FO |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42889-B | 320FT42889B | - | FT | dP Flow Transmitter with seal | Flow | 320-F -42889 | 31 | PID-320402801 | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | OFI TO X4201 REAC B CIRC | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 2 | B-ALARM | - | [13 empty] | 320FT42889B | [15 empty] | - | - | - | - | - | 0 | 2 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | N | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -42889 | 320FV42889 | - | FV | Control Valve | Control Valve | 320-F -42889 | 80 | PID-320402801 | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | OFI TO X4201 REAC B CIRC | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 3 | - | - | [13 empty] | 320FV42889 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FO |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -42890 | 320PT42890 | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -42890 | 30 | PID-320402801 | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | OFI TO X4201 REAC B CIRC | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 4 | - | - | [13 empty] | 320PT42890 | [15 empty] | - | - | - | - | - | 0 | 65 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-TT -42409-A | 320TT42409A | - | TT | Temperature Transmitter | Temperature | 320-T -42409 | 30 | PID-320402401 | 320-R-4201 LOOP REACTOR B LEG .7 | R-4201 REAC B LEG .7 | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS |  | Pair 5 | - | - | [13 empty] | 320TT42409A | [15 empty] | - | - | - | - | - | -50 | 165 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42318-C | 320XLS42318C | - | XLS | Position Limit Switch | General | 320-X -42318 | 30 | PID-320402301 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-A FLASHLINE HEATER | RIB FLUSH TO R-4201-A | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 6 | - | 320-UC-42011 | [13 empty] | 320XLS42318C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42318-O | 320XLS42318O | - | XLS | Position Limit Switch | General | 320-X -42318 | 31 | PID-320402301 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-A FLASHLINE HEATER | RIB FLUSH TO R-4201-A | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 7 | - | 320-UC-42011 | [13 empty] | 320XLS42318O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42319-C | 320XLS42319C | - | XLS | Position Limit Switch | General | 320-X -42319 | 30 | PID-320402301 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | RIB FLUSH TO R-4201-B | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 8 | - | 320-UC-42011 | [13 empty] | 320XLS42319C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42319-O | 320XLS42319O | - | XLS | Position Limit Switch | General | 320-X -42319 | 31 | PID-320402301 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | RIB FLUSH TO R-4201-B | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 9 | - | 320-UC-42011 | [13 empty] | 320XLS42319O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XPT -42319 | 320XPT42319 | - | XPT | Pressure Transmitter | General | 320-X -42319 | 32 | PID-320402301 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | RIB FLUSH TO R-4201-B | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | 10.0 | - | - | [13 empty] | 320XPT42319 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42418-C | 320XLS42418C | - | XLS | Position Limit Switch | General | 320-X -42418 | 30 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | RIB FLUSH TO E-4221-F | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 11 | - | 320-UC-42011 | [13 empty] | 320XLS42418C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42418-O | 320XLS42418O | - | XLS | Position Limit Switch | General | 320-X -42418 | 31 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | RIB FLUSH TO E-4221-F | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 12 | - | 320-UC-42011 | [13 empty] | 320XLS42418O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XPT -42418 | 320XPT42418 | - | XPT | Pressure Transmitter | General | 320-X -42418 | 32 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | RIB FLUSH TO E-4221-F | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 13 | - | - | [13 empty] | 320XPT42418 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42419-C | 320XLS42419C | - | XLS | Position Limit Switch | General | 320-X -42419 | 30 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | RIB FLUSH TO E-4221-E | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 14 | - | 320-UC-42011 | [13 empty] | 320XLS42419C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XLS -42419-O | 320XLS42419O | - | XLS | Position Limit Switch | General | 320-X -42419 | 31 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | RIB FLUSH TO E-4221-E | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | DIR | - | - | IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 15 | - | 320-UC-42011 | [13 empty] | 320XLS42419O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XPT -42419 | 320XPT42419 | - | XPT | Pressure Transmitter | General | 320-X -42419 | 32 | PID-320402401 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | RIB FLUSH TO E-4221-E | - |  | 320 | New | TYPICAL H2 | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 16 | - | - | [13 empty] | 320XPT42419 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZPT -42310 | 320ZPT42310 | - | ZPT | Pressure Transmitter | Pressure | 320-Z -42310 | 35 | PID-320402301 | 320-R-4201 POLYMER SLURRY TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 PSLY TO D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 17 | - | - | [13 empty] | 320ZPT42310 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZPT -42410 | 320ZPT42410 | - | ZPT | Pressure Transmitter | Pressure | 320-Z -42410 | 35 | PID-320402401 | 320-R-4201 LEG.8 POLYMER SLURRY TO 320-D-40232 REACTOR DUMP VESSEL | R-4201 L8 PSLY/D-40232 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 18 | - | - | [13 empty] | 320ZPT42410 | [15 empty] | - | - | - | - | - | 0 | 12 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-AXS -42250-A | 320AXS42250A | - | AXS | General Fault Switch | General | 320-A -42250 | 30 | PID-320401301 | 320-R-4101 LOOP REACTOR A LEG.6 | R-4101 REAC A LEG.6 | - |  | 320 | New | - | - | LP | DCS | - | DI | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | 320-JE-0083 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0083 | Pair 19 | - | [14 empty] | 320AXS42250A | [15 empty] | T | FAULT | NORMAL | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42044 | 320FT42044 | - | FT | Coriolis Meter | Flow | 320-F -42044 | 30 | PID-320402001 | RECYCLE ISOBUTANE TO 320-C-5041 DEHEX COLUMN | RIB TO C-5041 DEHEX COL | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | 230VAC | 4-Wire | No | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 1 | - | - | [13 empty] | 320FT42044 | [15 empty] | - | - | - | - | - | 0 | 21 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -42044 | 320FV42044 | - | FV | Control Valve | Control Valve | 320-F -42044 | 80 | PID-320402001 | RECYCLE ISOBUTANE TO 320-C-5041 DEHEX COLUMN | RIB TO C-5041 DEHEX COL | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 2 | - | - | [13 empty] | 320FV42044 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42048 | 320FT42048 | - | FT | Coriolis Meter | Flow | 320-F -42048 | 30 | PID-320402001 | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | TRTD RIB TO R-4201 HDR | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | 230VAC | 4-Wire | No | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 3 | A-CONTROL | - | [13 empty] | 320FT42048 | [15 empty] | - | - | - | - | - | 0 | 41 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -42048 | 320FV42048 | - | FV | Control Valve | Control Valve | 320-F -42048 | 80 | PID-320402001 | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | TRTD RIB TO R-4201 HDR | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 4 | - | - | [13 empty] | 320FV42048 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42049-A | 320FT42049A | 320-FT -42049 | FT | Coriolis Meter | Flow | 320-F -42049 | 30 | PID-320402002 | HEXENE TREATED FROM HEXENE FEED PUMPS 320-G-2032-A/B | HXE TRTD FRM G-2032-A/B | - |  | 320 | Modified | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | 230VAC | 4-Wire | No | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 5 | - | - | [13 empty] | 320FT42049A | [15 empty] | - | - | - | - | - | 0 | 0.6 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FV -42049-A | 320FV42049A | - | FV | Control Valve | Control Valve | 320-F -42049 | 80 | PID-320402002 | HEXENE TREATED FROM HEXENE FEED PUMPS 320-G-2032-A/B | HXE TRTD FRM G-2032-A/B | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 6 | - | - | [13 empty] | 320FV42049A | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42058 | 320FT42058 | - | FT | Coriolis Meter | Flow | 320-F -42058 | 30 | PID-320402002 | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | S2011 TRTD ETH/R4201 L2 | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | 230VAC | 4-Wire | No | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 7 | A-CONTROL | - | [13 empty] | 320FT42058 | [15 empty] | - | - | - | - | - | 0 | 41 | ton/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42060 | 320FT42060 | - | FT | Coriolis Meter | Flow | 320-F -42060 | 30 | PID-320402001 | RECYCLE ISOBUTANE FLUSH TO 320-R-4201 REACTOR TOP | RIB FLUSH TO R-4201 TOP | - |  | 320 | Modified | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | 230VAC | 4-Wire | No | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 8 | - | - | [13 empty] | 320FT42060 | [15 empty] | - | - | - | - | - | 0 | 480 | kg/h |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -42047 | 320PT42047 | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -42047 | 0 | PID-320402001 | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 | TRTD RIB TO R-4201 | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 9 | - | - | [13 empty] | 320PT42047 | [15 empty] | - | - | - | - | - | 0 | 75 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -42055 | 320PT42055 | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -42055 | 0 | PID-320402002 | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | S2011 TRTD ETH/R4201 L2 | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 10 | - | - | [13 empty] | 320PT42055 | [15 empty] | - | - | - | - | - | 0 | 65 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-FT -42044 | 320PT42062A | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -42062 | 43 | PID-320402001 | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | TRTD RIB TO R-4201 HDR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 11 | - | - | [13 empty] | 320PT42062A | [15 empty] | - | - | - | - | - | 0 | 75 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PT -42062-B | 320PT42062B | - | PT | Pressure Transmitter with Seal | Pressure | 320-P -42062 | 31 | PID-320402001 | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | TRTD RIB TO R-4201 HDR | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 12 | - | - | [13 empty] | 320PT42062B | [15 empty] | - | - | - | - | - | 0 | 75 | bar-g |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PV -42207 | 320PV42207 | - | PV | Control Valve | Control Valve | 320-P -42207 | 80 | PID-320402201 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-B FLASHLINE HEATER | RIB FLUSH TO E-4221-B | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 13 | - | - | [13 empty] | 320PV42207 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PZT -42207 | 320PZT42207 | - | PZT | Position Transmitter | General | 320-P -42207 | 30 | PID-320402201 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-B FLASHLINE HEATER | RIB FLUSH TO E-4221-B | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 14 | - | 320-UC-42011 | [13 empty] | 320PZT42207 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PV -42209 | 320PV42209 | - | PV | Control Valve | Control Valve | 320-P -42209 | 80 | PID-320402201 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-A FLASHLINE HEATER | RIB FLUSH TO E-4221-A | - |  | 320 | New | - | - | L | DCS | - | AOR | - | 4-20 ma HART | NON-IS | - | 2-Wire | - | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 15 | - | - | [13 empty] | 320PV42209 | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | FC |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PZT -42209-C | 320PZT42209C | - | PZT | Position Transmitter | General | 320-P -42209 | 30 | PID-320402201 | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-A FLASHLINE HEATER | RIB FLUSH TO E-4221-A | - |  | 320 | New | - | - | L | DCS | - | AIR | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 16 | - | 320-UC-42011 | [13 empty] | 320PZT42209C | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-PDT -42054 | 320PDT42054 | - | PDT | Diff.Pressure Transmitter with Seal | Pressure | 320-PD-42054 | 0 | PID-320402002 | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | S2011 TRTD ETH/R4201 L2 | - |  | 320 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 17 | - | - | [13 empty] | 320PDT42054 | [15 empty] | - | - | - | - | - | 0 | 10 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZLS -42050-C | 320ZLS42050C | - | ZLS | Position Limit Switch | General | 320-Z -42050 | 30 | PID-320402002 | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | S2011 TRTD ETH/R4201 L2 | - |  | 320 | New | TYPICAL A2 | - | L | DCS | - | DI | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0087 | - | 320-CE-0087 | Pair 18 | - | - | [13 empty] | 320ZLS42050C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZLS -42050-O | 320ZLS42050O | - | ZLS | Position Limit Switch | General | 320-Z -42050 | 31 | PID-320402002 | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | S2011 TRTD ETH/R4201 L2 | - |  | 320 | New | TYPICAL A2 | - | L | DCS | - | DI | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 320-JE-0087 | 24PX1MM2/FR/IND&OS/ARM/NIS | 320-CE-0087 | Pair 19 | - | - | [13 empty] | 320ZLS42050O | [15 empty] | F | OPEN | NOT OPEN | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -20202 | 320XYV20202 | - | XYV | Solenoid Valve | Control Valve | 320-X -20202 | 70 | PID-320200202 | HEXENE FROM 320-G-2032-B DISCHARGE | HXE FRM G-2032-B DISCH | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0005 | 12PX2.5MM2/FR/ARM/NIS | 320-CS-0005 | Pair 2 | B | 320-UC-20070 | [13 empty] | 320XYV20202 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40030 | 320XYV40030 | - | XYV | Solenoid Valve | Control Valve | 320-X -40030 | 0 | PID-320400001 | LPN TO 320-D-4143-AOLEFINE FREE ISOBUTANE TREATER | LPN TO D-4143-A OFI TRT | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0005 | 12PX2.5MM2/FR/ARM/NIS | 320-CS-0005 | Pair 3 | - | 320-UC-40015 | [13 empty] | 320XYV40030 | [15 empty] | - | CLOSE | OPEN | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40102 | 320XYV40102 | - | XYV | Solenoid Valve | Control Valve | 320-X -40102 | 70 | PID-320400102 | 320-G-4142 B OLEFIN FREE ISOBUTANE PUMP DISCHARGE | G-4142 B OFI PMP DISCH | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0005 | 12PX2.5MM2/FR/ARM/NIS | 320-CS-0005 | Pair 4 | B | 320-UC-41050 | [13 empty] | 320XYV40102 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40301 | 320XYV40301 | - | XYV | Solenoid Valve | Control Valve | 320-X -40301 | 70 | PID-320400302 | 320-G-4242-B RECYCLE ISOBUTANE PUMP DISCHARGE | G-4242-B RIB DISCH | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0005 | 12PX2.5MM2/FR/ARM/NIS | 320-CS-0005 | Pair 5 | B | 320-UC-42050 | [13 empty] | 320XYV40301 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40345 | 320XYV40345 | - | XYV | Solenoid Valve | Control Valve | 320-X -40345 | 70 | PID-320400301 | OLEFIN FREE ISOBUTANE TO 320-D-4242 RECYCLE ISOBUTANE VESSEL | OFI TO D-4242 RIB VESL | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0005 | 12PX2.5MM2/FR/ARM/NIS | 320-CS-0005 | Pair 6 | - | 320-UC-40033 | [13 empty] | 320XYV40345 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40529-C | 320XYV40529C | - | XYV | Solenoid Valve | Control Valve | 320-X -40529 |  | PID-320400501 | 320-R-4101 VENT TO 320-D-4023 REACTOR DUMP VESSEL | R-4101 VENT TO D-4023 | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 1 | - | 320-UC-40051 | [13 empty] | 320XYV40529C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40529-O | 320XYV40529O | - | XYV | Solenoid Valve | Control Valve | 320-X -40529 |  | PID-320400501 | 320-R-4101 VENT TO 320-D-4023 REACTOR DUMP VESSEL | R-4101 VENT TO D-4023 | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 2 | - | 320-UC-40051 | [13 empty] | 320XYV40529O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40551-C | 320XYV40551C | - | XYV | Solenoid Valve | Control Valve | 320-X -40551 |  | PID-320400501 | 320-R-4201 VENT TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 VENT TO D-4023 | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 3 | - | 320-UC-40051 | [13 empty] | 320XYV40551C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -40551-O | 320XYV40551O | - | XYV | Solenoid Valve | Control Valve | 320-X -40551 |  | PID-320400501 | 320-R-4201 VENT TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 VENT TO D-4023 | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 4 | - | 320-UC-40051 | [13 empty] | 320XYV40551O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42901-AC | 320XYV42901AC | - | XYV | Solenoid Valve | Control Valve | 320-X -42901 |  | PID-320403301 | 320-E-4221A FLASH LINE HEATER A | E-4221-A FLASHLINE HTR | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 5 | A | 320-UC-42091 | [13 empty] | 320XYV42901AC | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42901-AO | 320XYV42901AO | - | XYV | Solenoid Valve | Control Valve | 320-X -42901 |  | PID-320403301 | 320-E-4221A FLASH LINE HEATER A | E-4221-A FLASHLINE HTR | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 6 | A | 320-UC-42091 | [13 empty] | 320XYV42901AO | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42903-AC | 320XYV42903AC | - | XYV | Solenoid Valve | Control Valve | 320-X -42903 |  | PID-320403303 | 320-E-4221C FLASH LINE HEATER C | E-4221C FLASH LINE HTR C | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 7 | C | 320-UC-42091 | [13 empty] | 320XYV42903AC | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42903-AO | 320XYV42903AO | - | XYV | Solenoid Valve | Control Valve | 320-X -42903 |  | PID-320403303 | 320-E-4221C FLASH LINE HEATER C | E-4221C FLASH LINE HTR C | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 8 | C | 320-UC-42091 | [13 empty] | 320XYV42903AO | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42905-AC | 320XYV42905AC | - | XYV | Solenoid Valve | Control Valve | 320-X -42905 |  | PID-320403305 | 320-E-4221E FLASH LINE HEATER E | E-4221-E FLASHLINE HTR | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 9 | E | 320-UC-42091 | [13 empty] | 320XYV42905AC | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42905-AO | 320XYV42905AO | - | XYV | Solenoid Valve | Control Valve | 320-X -42905 |  | PID-320403305 | 320-E-4221E FLASH LINE HEATER E | E-4221-E FLASHLINE HTR | - |  | 320 | New | TYPICAL F2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 10 | E | 320-UC-42091 | [13 empty] | 320XYV42905AO | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40511-C | 320ZYV40511C | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40511 |  | PID-320400501 | POLYMER SLURRY FROM LEG 7&8 320-R-4101 TO 320-D-4023 REACTOR DUMP VESSEL | R-4101 L7&8 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 11 | - | 320-UC-40051 | [13 empty] | 320ZYV40511C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40511-O | 320ZYV40511O | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40511 |  | PID-320400501 | POLYMER SLURRY FROM LEG 7&8 320-R-4101 TO 320-D-4023 REACTOR DUMP VESSEL | R-4101 L7&8 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 12 | - | 320-UC-40051 | [13 empty] | 320ZYV40511O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40512-C | 320ZYV40512C | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40512 |  | PID-320400501 | POLYMER SLURRY FROM LEG 7&8 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L7&8 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 13 | - | 320-UC-40051 | [13 empty] | 320ZYV40512C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40512-O | 320ZYV40512O | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40512 |  | PID-320400501 | POLYMER SLURRY FROM LEG 7&8 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L7&8 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 14 | - | 320-UC-40051 | [13 empty] | 320ZYV40512O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40525-C | 320ZYV40525C | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40525 |  | PID-320400501 | POLYMER SLURRY FROM LEG 5&6 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L5&6 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 15 | - | 320-UC-40051 | [13 empty] | 320ZYV40525C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40525-O | 320ZYV40525O | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40525 |  | PID-320400501 | POLYMER SLURRY FROM LEG 5&6 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L5&6 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 16 | - | 320-UC-40051 | [13 empty] | 320ZYV40525O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40526-C | 320ZYV40526C | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40526 |  | PID-320400501 | POLYMER SLURRY FROM LEG 1&2 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L1&2 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 17 | - | 320-UC-40051 | [13 empty] | 320ZYV40526C | [15 empty] | - | CLOSE | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-ZYV -40526-O | 320ZYV40526O | - | ZYV | Solenoid Valve | Control Valve | 320-Z -40526 |  | PID-320400501 | POLYMER SLURRY FROM LEG 1&2 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | R-4201 L1&2 PSLY/D-4023 | - |  | 320 | New | TYPICAL L2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0008 | 24PX2.5MM2/FR/ARM/NIS | 320-CS-0008 | Pair 18 | - | 320-UC-40051 | [13 empty] | 320ZYV40526O | [15 empty] | - | OPEN | NO ACTION | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42170 | 320XYV42170 | - | XYV | Solenoid Valve | Control Valve | 320-X -42170 | 70 | PID-320402101 | VENT TO DUMP VESSEL | VENT TO DMP VESL | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0022 | 06PX2.5MM2/FR/ARM/NIS | 320-CS-0022 | Pair 1 | - | 320-UC-42031 | [13 empty] | 320XYV42170 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42288 | 320XYV42288 | - | XYV | Solenoid Valve | Control Valve | 320-X -42288 | 70 | PID-320402201 | 320-R-4201 RECYCLE ISOBUTANE FLUSH TO 320-D-4023 DUMP VESSEL | R-4201 RIB FLUSH/D-4023 | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0022 | 06PX2.5MM2/FR/ARM/NIS | 320-CS-0022 | Pair 2 | - | 320-UC-42031 | [13 empty] | 320XYV42288 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42302 | 320XYV42302 | - | XYV | Solenoid Valve | Control Valve | 320-X -42302 | 70 | PID-320402301 | 320-R-4201 LOOP REACTOR B LEG .6 TO 320-D-4023 DUMP VESSEL | R-4201 L6 TO D-4023 | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0022 | 06PX2.5MM2/FR/ARM/NIS | 320-CS-0022 | Pair 3 | - | 320-UC-42031 | [13 empty] | 320XYV42302 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-XYV -42402 | 320XYV42402 | - | XYV | Solenoid Valve | Control Valve | 320-X -42402 | 70 | PID-320402401 | 320-R-4201 RECYCLE ISOBUTANE VENT TO 320-D-4023 DUMP VESSEL | R-4201 RIB VENT/D-4023 | - |  | 320 | New | TYPICAL E2 | - | L | DCS | - | DOR | - | - | NON-IS | - | Volt-contact | - | - | - | - | 320-JS-0022 | 06PX2.5MM2/FR/ARM/NIS | 320-CS-0022 | Pair 4 | - | 320-UC-42031 | [13 empty] | 320XYV42402 | [15 empty] | - | OPEN | CLOSE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 01 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-LI -00032-L | 500LI00032L | - | LI | Local Indicator | General | 500-L -00032 | 90 | PID-500000401 | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | BA-0001 OILY WTR PIT | - |  | 500 | New | - | - | L | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-JE-0013 | 06PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0013 | Pair 1 | - | - | [13 empty] | 500LI00032L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | - | 2024-06-14 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-LT -00032 | 500LT00032 | - | LT | Radar Level Transmitter | Level | 500-L -00032 | 30 | PID-500000401 | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | BA-0001 OILY WTR PIT | - |  | 500 | New | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 500-JE-0013 | 06PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0013 | Pair 2 | - | - | [13 empty] | 500LT00032 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | - | 2024-06-14 | - | - | [5 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-LI -00051-L | 500LI00051L | 500-DUMMY-TAG-100 | LI | Local Indicator | General | 500-L -00051 | 90 | PID-500000401 | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | BA-0001 OILY WTR PIT | - |  | 500 | Modified | - | - | L | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-JE-0013 | 06PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0013 | Pair 3 | - | - | [13 empty] | 500LI00051L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag Renamed, Wiring Updated | 2025-06-03 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-LT -00051 | 500LT00051 | 500-DUMMY-TAG-304 | LT | Radar Level Transmitter | Level | 500-L -00051 | 30 | PID-500000401 | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | BA-0001 OILY WTR PIT | - |  | 500 | Modified | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 500-JE-0013 | 06PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0013 | Pair 4 | - | - | [13 empty] | 500LT00051 | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.02 | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Tag Renamed. Wiring Updated. Range updated. | 2025-06-03 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XS -00322 | 500XS00322 | - | XS | Switch | General | 500-X -00322 | 34 | PID-500000301 | EARTHING CONNECTION | GRND CONN | - |  | 500 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | 500-JE-0015 | 12PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0015 | Pair 1 | - | 500-UC-00030 | [13 empty] | 500XS00322 | [15 empty] | F | ACTIVE | NOT ACTIVE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Wiring Updated | 2025-07-16 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XS -00612 | 500XS00612 | - | XS | Switch | General | 500-X -00612 | 34 | PID-500000601 | EARTHING CONNECTION | GRND CONN | - |  | 500 | New | - | - | L | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | 500-JE-0015 | 12PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0015 | Pair 2 | - | 500-UC-00060 | [13 empty] | 500XS00612 | [15 empty] | F | ACTIVE | NOT ACTIVE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Wiring Updated | 2025-07-16 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XS -00711 | 500XS00711 | - | XS | Switch | General | 500-X -00711 | 34 | PID-500000701 | EARTHING CONNECTION | GRND CONN | - |  | 500 | New | - | - | L | DCS | - | Dir | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | 500-JE-0015 | 12PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0015 | Pair 3 | - | 500-UC-00070 | [13 empty] | 500XS00711 | [15 empty] | F | ACTIVE | NOT ACTIVE | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Wiring Updated | 2025-07-16 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-PDT -00611 | 500PDT00611 | 500-DUMMY-TAG-71 | PDT | Diff. Pressure Transmitter with Seal | Pressure | 500-PD-00611 | 30 | PID-500000601 | ZTUA-0004 CAUSTIC SODA UNLOADING TO G-0004 | ZTUA-0004 CAU TO G-0004 | - |  | 500 | Modified | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 500-JE-0015 | 12PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0015 | Pair 4 | - | - | [13 empty] | 500PDT00611 | [15 empty] | - | - | - | - | - | 0 | 1 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-PDT -00712 | 500PDT00712 | 500-DUMMY-TAG-72 | PDT | Diff. Pressure Transmitter with Seal | Pressure | 500-PD-00712 | 30 | PID-500000701 | ZTUA-0006 HEXENE-1 TO G-0005 | ZTUA-0006 HXE TO G-0005 | - |  | 500 | Modified | - | - | L | DCS | - | AI | - | 4-20 ma HART | NON-IS | - | 2-Wire | Yes | - | - | - | 500-JE-0015 | 12PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-0015 | Pair 5 | - | - | [13 empty] | 500PDT00712 | [15 empty] | - | - | - | - | - | 0 | 1 | bar |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-FI -00051-L | 500FI00051L | - | FI | Local Panel Indicator | General | 500-F -00051 | 2 | PID-500000301 | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | IBT TO BULLET 440-D-2014 | - |  | 500 | Modified | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 1 | - | - | [13 empty] | 500FI00051L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | Y | X | X | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-FI -00311-L | 500FI00311L | - | FI | Local Panel Indicator | General | 500-F -00311 | 2 | PID-500000301 | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | ZTUA-0002 IBT UNLD/G-001 | - |  | 500 | Modified | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 2 | - | - | [13 empty] | 500FI00311L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.05 | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-PI -00313-L | 500PI00313L | - | PI | Local Panel Indicator | General | 500-P -00313 | 40 | PID-500000301 | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | ZTUA-0002 IBT UNLD/G-001 | - |  | 500 | Modified | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 3 | - | - | [13 empty] | 500PI00313L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | Y | X | X | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-HS -00053-L | 500HS00053L | - | HS | Hand Switch | General | 500-H -00053 | 83 | PID-500000301 | UNLOADING START | UNLD START | - |  | 500 | Modified | - | - | LP | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 4 | - | 500-UC-00030 | [13 empty] | 500HS00053L | [15 empty] | F | START | NO ACTION | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-HS -00054-L | 500HS00054L | - | HS | Hand Switch | General | 500-H -00054 | 83 | PID-500000301 | UNLOADING STOP | UNLD STOP | - |  | 500 | Modified | - | - | LP | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 5 | - | 500-UC-00030 | [13 empty] | 500HS00054L | [15 empty] | F | NO ACTION | STOP | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-HS -00068-L | 500HS00068L | - | HS | Hand Switch | General | 500-H -00068 | 83 | PID-500000301 | LOCAL OPERATOR PERMISSIVE FOR UNLOADING | LOCAL PERM FOR UNLD | - |  | 500 | Modified | - | - | LP | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 6 | - | 500-UC-00030 | [13 empty] | 500HS00068L | [15 empty] | F | PERMISSIVE | NO PERM | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated, On off state updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-PI -00321-L | 500PI00321L | - | PI | Local Panel Indicator | General | 500-P -00321 |  | PID-500000301 | HEADER LOW PRESSURE NITROGEN TO FLARE | HDR LPN TO FLR | - |  | 500 | New | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 7 | - | - | [13 empty] | 500PI00321L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | [9 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-QI -00051-L | 500QI00051L | 500-FQI -00051-L | QI | Local Panel Indicator | General | 500-F -00051 |  | PID-500000301 | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | IBT TO BULLET 440-D-2014 | - |  | 500 | Modified | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 8 | - | - | [13 empty] | 500QI00051L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag Renamed | 2025-07-16 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-TI -00002-L | 500TI00002L | - | TI | Local Panel Indicator | General | 500-T -00002 |  | PID-500000301 | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | IBT TO BULLET 440-D-2014 | - |  | 500 | New | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 11 | - | - | [13 empty] | 500TI00002L | [15 empty] | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | [9 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-QI -20044-L | 440QI20044L | 440-FQI -20044-L | QI | Local Panel Indicator | General | 440-F -20044 |  | PID-500000301 | ISOBUTANE BULLET VOLUME INCREASE | IBT BULLET VOL INCREASE | - |  | 440 | Modified | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 12 | - | - | [13 empty] | 440QI20044L | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Tag Renamed. Range updated. | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-TI -20044-L | 440TI20044L | - | TI | Local Panel Indicator | General | 440-T -20044 |  | PID-500000301 | ISOBUTANE BULLET 440-D-2014 | IBT BULLET 440-D-2014 | - |  | 440 | New | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 13 | - | - | [13 empty] | 440TI20044L | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-PI -20077-L | 440PI20077L | - | PI | Local Panel Indicator | General | 440-P -20077 |  | PID-500000301 | ISOBUTANE BULLET 440-D-2014 | IBT BULLET 440-D-2014 | - |  | 440 | New | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 14 | - | - | [13 empty] | 440PI20077L | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-LI -20044-L | 440LI20044L | - | LI | Local Panel Indicator | General | 440-L -20044 |  | PID-500000301 | ISOBUTANE BULLET 440-D-2014 | IBT BULLET 440-D-2014 | - |  | 440 | New | - | - | LP | DCS | - | AO | - | 4-20 ma | NON-IS | - | 2-Wire | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 15 | - | - | [13 empty] | 440LI20044L | [15 empty] | - | - | - | - | - | 0 | 100 | % |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B+ | PDR-1 | Range updated | 2025-10-05 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-HS -00351-L | 500HS00351L | 500-DUMMY-TAG-75 | HS | Local Panel Hand Switch | General | 500-H -00351 | 83 | PID-500000301 | LP#3 LAMP TEST | LP#3 LAMP TEST | - |  | 500 | Modified | - | - | LP | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NO | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 16 | - | - | [13 empty] | 500HS00351L | [15 empty] | F | LAMP ON | LAMP OFF | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-MHL -G0001-RL | 500MHLG0001RL | 500-DUMMY-TAG-706 | MHL | Motor Local / Remote Indication | General | 500-M -G0001 | 25 | PID-500000301 | 500-G-0001 MOT REMOTE INDIC | G-0001 MOT REM INDIC | 500-G-0001 | ISOBUTANE UNLOADING PUMP | 500 | Modified | - | PKG-019003 | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX1MM2/FR/IND&OS/ARM/NIS | 500-CE-LP-0003-A | Pair 19 | - | - | [13 empty] | 500MHLG0001RL | [15 empty] | - | REMOTE | NO ACTION | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag renamed | 2025-06-20 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XA -00322-L | 500XA00322L | - | XA | Alarm | General | 500-X -00322 | 34 | PID-500000301 | EARTHING CONNECTION | GRND CONN | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 1 | - | 500-UC-00030 | [13 empty] | 500XA00322L | [15 empty] | - | LAMP ON | LAMP OFF | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XA -00323-L | 500XA00323L | - | XA | Alarm | General | 500-X -00323 | 34 | PID-500000301 | ISOBUTANE ARM PARKING POSITION | IBT ARM PARKING | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 2 | - | 500-UC-00030 | [13 empty] | 500XA00323L | [15 empty] | - | LAMP ON | LAMP OFF | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 |  | 2025-04-23 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XA -00324-L | 500XA00324L | - | XA | Alarm | General | 500-X -00324 | 34 | PID-500000301 | ISOBUTANE ARM COUPLING | IBT ARM COUPLING | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 3 | - | 500-UC-00030 | [13 empty] | 500XA00324L | [15 empty] | - | LAMP ON | LAMP OFF | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-MXL -G0001-L | 500MXLG0001L | 500-DUMMY-TAG-91 | MXL | Motor Running Indication | General | 500-M -G0001 |  | PID-500000301 | 500-G-0001 MOT RUNNING INDIC | G-0001 MOT RUNNING INDIC | 500-G-0001 | ISOBUTANE UNLOADING PUMP | 500 | Modified | - | PKG-019003 | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 5 | - | - | [13 empty] | 500MXLG0001 | [15 empty] | - | RUNNING | NOT RUNNING | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Tag Renamed, IO Type Changed to Non-Redundant, Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-QAX -00051-L | 500QAX00051L | 500-FQAX -00051-L | QAX | Discrepancy Alarm | General | 500-F -00051 |  | PID-500000301 | DISCREPANCY BETWEEN 500-FQI-00051 and 440-FQI-00XXX | DISCR FQI-00051FQI-00XXX | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 6 | - | - | [13 empty] | 500QAX00051L | [15 empty] | - | ALARM | NORMAL | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag Renamed | 2025-07-16 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-ZLO -00311-L | 500ZLO00311L | 500-DUMMY-TAG-99 | ZLO | Position Indication Open | General | 500-Z -00311 |  | PID-500000301 | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | ZTUA-0002 IBT UNLD/G-001 | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 8 | - | - | - | [12 empty] | 500ZLO00311L | [15 empty] | - | OPEN | NOT OPEN | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Tag Renamed, IO Type Changed to Non-Redundant, Wiring Updated | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-ZLO -00052-L | 500ZLO00052L | 500-DUMMY-TAG-98 | ZLO | Position Indication Open | General | 500-Z -00052 |  | PID-500000301 | UNLOADING BAY ISOBUTANE TO 440-D-2014 | UNLD BAY IBT/440-D-2014 | - |  | 500 | Modified | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 10 | - | - | - | [12 empty] | 500ZLO00052L | [15 empty] | - | OPEN | NOT OPEN | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Tag Renamed | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-ZLO -20057-L | 440ZLO20057L | - | ZLO | Position Indication Open | General | 440-Z -20057 |  | PID-500000301 | 440-ZV-20057 OPEN POSITION INDICATION | 440-ZV-20057 OPN INDIC | - |  | 440 | New | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 12 | - | - | - | [12 empty] | 440ZLO20057L | [15 empty] | - | OPEN | NOT OPEN | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | [9 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 440-ZLO -20027-L | 440ZLO20027L | - | ZLO | Position Indication Open | General | 440-Z -20027 |  | PID-500000301 | 440-ZV-20027 OPEN POSITION INDICATION | 440-ZV-20027 OPN INDIC | - |  | 440 | New | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 14 | - | - | - | [12 empty] | 440ZLO20027L | [15 empty] | - | OPEN | NOT OPEN | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | [9 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XA -00331-L | 500XA00331L | - | XA | Alarm | General | 500-X -00331 | 34 | PID-500000301 | DCS OPERATOR PERMISSIVE | DCS OPR PERM | - |  | 500 | New | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 15 | - | - | [13 empty] | 500XA00331L | [15 empty] | - | PERMISSIVE | NO ACTION | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 02 | PDR-1 | - | 2024-11-15 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-MXA -G0001-L | 500MXAG0001L | 500-DUMMY-TAG-90 | MXA | Motor Fault Alarm | General | 500-M -G0001 |  | PID-500000301 | 500-G-0001 MOT FAULT INDIC | G-0001 MOT FAULT INDIC | 500-G-0001 | ISOBUTANE UNLOADING PUMP | 500 | Modified | - | PKG-019003 | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 16 | - | - | [13 empty] | 500MXAG0001 | [15 empty] | - | FAULT | NORMAL | LOG | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 04 | PDR-1 | Cable name, Formation and Pair Number Updated | [8 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-MHL -G0001-LL | 500MHLG0001LL | 500-MHL -G0001-L | MHL | Motor Local / Remote Indication | General | 500-M -G0001 | 24 | PID-500000301 | 500-G-0001 MOT LOCAL INDIC | G-0001 MOT LOC INDIC | 500-G-0001 | ISOBUTANE UNLOADING PUMP | 500 | Modified | - | PKG-019003 | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 17 | - | - | [13 empty] | 500MHLG0001LL | [15 empty] | - | LOCAL | NO ACTION | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag renamed | 2025-06-20 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-XA -00341-L | 500XA00341L | 500-DUMMY-TAG-703 | XA | Alarm | General | 500-X -00341 | 34 | PID-500000301 | NITROGEN ARM PARKING POSITION | N2 ARM PARKING | - |  | 500 | New | - | - | LP | DCS | - | DO | - | - | NON-IS | - | Volt-contact | - | - | - | - | 500-LP-0003 | 24PX2.5MM2/FR/ARM/NIS | 500-CE-LP-0003-B | Pair 18 | - | 500-UC-00030 | [13 empty] | 500XA00341L | [15 empty] | - | LAMP ON | LAMP OFF | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Tag Renamed, Wiring Updated | 2025-04-23 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJA -00011-D | 500EJA00011D | - | EJA | Ventilation Failure | General | 500-E -00011-D |  | - | LIQUID HANDLING OPERATOR SHELTER HVAC COMMON FAILURE | LH OS HVAC COM FAIL | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | DI | DO | - | NON-IS | - | Voltfree-contact | - | - | - | NC | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 1 | - | - | [13 empty] | 500EJA00011D | [15 empty] | T | ALARM | NORMAL | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | New Tag Added | 2025-08-19 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJA -00024 | 500EJA00024 | - | EJA | Power failure switch | General | 500-E -00024 |  | - | LIQUID HANDLING OPERATOR SHELTER HVAC POWER LOSS ALARM | LH OS HVAC PWR LOSS | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | DI | DO | - | NON-IS | - | Voltfree-contact | - | - | - | NC | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 2 | - | - | [13 empty] | 500EJA00024 | [15 empty] | T | ALARM | NORMAL | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | New Tag Added | 2025-08-19 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-TT -00034 | 500TT00034 | - | TT | Temperature Transmitter | Temperature | 500-T -00034 |  | - | LIQUID HANDLING OPERATOR SHELTER HVAC RETURN DUCT TEMPERATURE INDICATION | LH OS VFD HVAC DUCT | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | AI | AO | 4-20 ma | NON-IS | - | 4-Wire | No | - | - | - | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 3 | - | - | - | [12 empty] | 500TT00034 | [15 empty] | - | - | - | - | - | 0 | 80 | °C |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | Wiring updated. | 2025-08-19 | - | - | [5 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-TAQ -00009-D | 500TAQ00009D |  | TAQ | Cumulative Temperature Alarm | General | 500-T -00009-D |  | - | LIQUID HANDLING OPERATOR SHELTER AREA HVAC CUMULATIVE TEMPERATURE ALARM | LH OS HVAC | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | DI | DO | - | NON-IS | - | Voltfree-contact | - | - | - | NC | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 4 | - | - | [13 empty] | 500TAQ00009D | [15 empty] | T | ALARM | NORMAL | ADVISORY | T | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | New Tag Added | 2025-08-19 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJR -00012-D | 500EJR00012D | - | EJR | Running Status | General | 500-E -00012-D |  | - | LIQUID HANDLING OPERATOR SHELTER HVAC RUNNING STATUS | WH HVAC RUN | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | AI | DO | - | NON-IS | - | Voltfree-contact | - | - | - | NC | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 5 | - | - | [13 empty] | 500EJR00012D | [15 empty] | F | RUNNING | NOT RUNNING | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | New Tag Added | 2025-08-19 | [7 empty] | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-DXLS -00003-C | 500DXLS00003C | - | DXLS | Cumulative Damper Close Position Feedback | General | 500-DX-00003 | 30 | - | LIQUID HANDLING OPERATOR SHELTER HVAC CUMULATIVE DAMPER CLOSE POSITION FEEDBACK | LH OS DMP CLS FB | 500-OS-02 | LIQUID HANDLING OPERATOR SHELTER | 500 | New | - | - | 500-OS-02 | DCS | HVAC | DI | DO | - | NON-IS | - | Voltfree-contact | - | - | - | NC | OS02-CP-01 | 12PX1MM2/FR/IND&OS/ARM/NIS | OS02-ICE-6001 | Pair 6 | - | - | [13 empty] | 500DXLS00003C | [15 empty] | F | CLOSED | NOT CLOSED | - | F | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | [14 empty] | - |  |  |  |  | - |  | 05B | PDR-1 | New Tag Added | 2025-08-16 | [7 empty] | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01001-T | 320EJA01001T | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01001 | - | - | P30-DCM-32001-01 TEMPERATURE | P30-DCM-32001-01 TEMPERATURE | P30-DCM-32001-01 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | AIR | - | RTD | NON-IS | - | 3-Wire | - | - | - | - | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01001T | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | 0 | 100 | deg C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01001-AC | 320EJA01001AC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01001 | - | - | P30-DCM-32001-01 230VAC FAIL | P30-DCM-32001-01 230VAC FAIL | P30-DCM-32001-01 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01001AC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01001-DC | 320EJA01001DC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01001 | - | - | P30-DCM-32001-01 24VDC FAIL | P30-DCM-32001-01 24VDC FAIL | P30-DCM-32001-01 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01001DC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01031-T | 320EJA01031T | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01031 | - | - | P30-DCS-32001-01 TEMPERATURE | P30-DCS-32001-01 TEMPERATURE | P30-DCS-32001-01 | DCS System Cabinet | 320 | New | - | - | PIB-30 | DCS | - | AIR | - | RTD | NON-IS | - | 3-Wire | - | - | - | - | - | 1TX1.3MM2/FR/OS/NIS | P30-ICE-0001 | Triad 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01031T | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | 0 | 100 | deg C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01031-AC | 320EJA01031AC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01031 | - | - | P30-DCS-32001-01 230VAC FAIL | P30-DCS-32001-01 230VAC FAIL | P30-DCS-32001-01 | DCS System Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | 2PX1.3MM2/FR/IND&OS/NIS | P30-ICE-0002 | Pair 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01031AC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01031-DC | 320EJA01031DC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01031 | - | - | P30-DCS-32001-01 24VDC FAIL | P30-DCS-32001-01 24VDC FAIL | P30-DCS-32001-01 | DCS System Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | 2PX1.3MM2/FR/IND&OS/NIS | P30-ICE-0002 | Pair 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01031DC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01004-T | 320EJA01004T | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01004 | - | - | P30-DCM-32001-04 TEMPERATURE | P30-DCM-32001-04 TEMPERATURE | P30-DCM-32001-04 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | AIR | - | RTD | NON-IS | - | 3-Wire | - | - | - | - | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01004T | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | 0 | 100 | deg C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01004-AC | 320EJA01004AC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01004 | - | - | P30-DCM-32001-04 230VAC FAIL | P30-DCM-32001-04 230VAC FAIL | P30-DCM-32001-04 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01004AC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-11 | PIB-30 | RA 320-01 | 320-EJA -01004-DC | 320EJA01004DC | - | EJA | Cabinet Diagnostic Alarm | General | 320-E -01004 | - | - | P30-DCM-32001-04 24VDC FAIL | P30-DCM-32001-04 24VDC FAIL | P30-DCM-32001-04 | DCS Marshalling Cabinet | 320 | New | - | - | PIB-30 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 320EJA01004DC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJA -01021-T | 500EJA01021T | - | EJA | Cabinet Diagnostic Alarm | General | 500-E -01021 | - | - | P24-DCM-50002-01 TEMPERATURE | P24-DCM-50002-01 TEMPERATURE | P24-DCM-50002-01 | DCS Marshalling Cabinet | 500 | New | - | - | PIB-24 | DCS | - | AIR | - | RTD | NON-IS | - | 3-Wire | - | - | - | - | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 500EJA01021T | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | 0 | 100 | deg C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJA -01021-AC | 500EJA01021AC | - | EJA | Cabinet Diagnostic Alarm | General | 500-E -01021 | - | - | P24-DCM-50002-01 230VAC FAIL | P24-DCM-50002-01 230VAC FAIL | P24-DCM-50002-01 | DCS Marshalling Cabinet | 500 | New | - | - | PIB-24 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 500EJA01021AC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OA-14 | PIB-24 | RA 500-02 | 500-EJA -01021-DC | 500EJA01021DC | - | EJA | Cabinet Diagnostic Alarm | General | 500-E -01021 | - | - | P24-DCM-50002-01 24VDC FAIL | P24-DCM-50002-01 24VDC FAIL | P24-DCM-50002-01 | DCS Marshalling Cabinet | 500 | New | - | - | PIB-24 | DCS | - | DIR | - | - | NON-IS | - | Voltfree-contact | - | - | - | NC | - | - | Internal Wiring | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 500EJA01021DC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T | ALARM | NORMAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -