## MDB-1
Process Function Type | Logic Number | Equipment Description | System 2 | Typical_No | Tag Service 1 and 2 | Junction Box / Panel | I/O Type Name 2 | P&ID | Equipment Name | Monitoring Frequency Of Interest (Hz) (MPS) | TAG NO. | Asset | Status | Equipment Type | System 1 (System) | Signal Type | Cable Spec | Voting | External Power Supply | Location | Cable No | Internal Loop Order | Loop Powered | Machine Level | WBS | Old Tag Number | TagNumber | Pair | Package Number | Contact Type | Point Type | Execution | Loop Name | Segregation | Instrument Type Description | Inst. Type | Signal Level | Service | IO TYPE
Flow | 320-UC-20060 |  | - | - | LPN TO F-2011 ETH HTR | 320-JE-0001 | - | PID-320200601 | - |  | 320-FT -20645-A | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320FT20645A | Pair 1 | - | - |  | NON-IS | 320-F -20645 | A-CONTROL | dP Flow Transmitter | FT | 2-Wire | LPN TO 320-F-2011 ETHYLENE TREATER REGENERATION HEATER | AIR
Control Valve | - |  | - | - | LPN TO F-2011 ETH HTR | 320-JE-0001 | - | PID-320200601 | - |  | 320-FV -20645 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 80 | - |  | 320 | - | 320FV20645 | Pair 2 | - | - |  | NON-IS | 320-F -20645 | A | Control Valve | FV | 2-Wire | LPN TO 320-F-2011 ETHYLENE TREATER REGENERATION HEATER | AOR
Flow | - |  | - | - | CWS TO K-8061-A/B | 320-JE-0001 | - | PID-320800001 | - |  | 320-FT -80002 | - | DELETED |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320FT80002 | Pair 3 | - | - |  | NON-IS | 320-F -80002 | - | dP Flow Transmitter | FT | 2-Wire | CWS TO K-8061-A/B | AI
Flow | - |  | - | - | K-8061A/B HPN CMPR SUCT | 320-JE-0001 | - | PID-320800001 | - |  | 320-FT -80004 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320FT80004 | Pair 4 | - | - |  | NON-IS | 320-F -80004 | - | dP Flow Transmitter | FT | 2-Wire | 320-K-8061A/B HP NITROGEN COMPRESSOR SUCTION | AI
Level | - | HP NITROGEN SURGE SUCTION DRUM | - | - | D-8060 HPN SRG SUCT DRM | 320-JE-0001 | - | PID-320800001 | 320-D-8060 |  | 320-LT -80001 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 40 | Yes |  | 320 | - | 320LT80001 | Pair 5 | - | - |  | NON-IS | 320-L -80001 | - | dP Level Transmitter | LT | 2-Wire | 320-D-8060 HP NITROGEN SURGE SUCTION DRUM | AI
Level | - | HP N ITROGEN DISCHARGE DRUM | - | - | D-8061 HPN DISCH DRM | 320-JE-0001 | - | PID-320800001 | 320-D-8061 |  | 320-LT -80002 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 40 | Yes |  | 320 | - | 320LT80002 | Pair 6 | - | - |  | NON-IS | 320-L -80002 | - | dP Level Transmitter | LT | 2-Wire | 320-D-8061 HP N ITROGEN DISCHARGE DRUM | AI
Level | - | POTABLE WATER VESSEL | - | - | D-8064 PWA VESL | 320-JE-0001 | - | PID-320801201 | 320-D-8064 |  | 320-LT -81209 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 40 | Yes |  | 320 | - | 320LT81209 | Pair 7 | - | - |  | NON-IS | 320-L -81209 | A-CONTROL | dP Level Transmitter | LT | 2-Wire | 320-D-8064 POTABLE WATER VESSEL | AIR
Level | - | SUSPECT CONDENSATE KO DRUM | - | - | D-8069 SSC KOD | 320-JE-0001 | - | PID-320803005 | 320-D-8069 |  | 320-LT -83050 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 0 | Yes |  | 320 | - | 320LT83050 | Pair 8 | - | - |  | NON-IS | 320-L -83050 | A-CONTROL | dP Level Transmitter with seal | LT | 2-Wire | 320-D-8069 SUSPECT CONDENSATE KNOCK OUT DRUM | AIR
Pressure | - |  | - | - | PLANT UNIT 1 LPN FRM OSBL | 320-JE-0001 | - | PID-320800001 | - |  | 320-PT -80002 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320PT80002 | Pair 9 | - | - |  | NON-IS | 320-P -80002 | - | Pressure Transmitter | PT | 2-Wire | PLANT UNIT 1 LPN FROM OSBL | AI
Pressure | 320-UC-80001 |  | - | - | K-8061A/B HPN CMPR DISCH | 320-JE-0001 | - | PID-320800001 | - |  | 320-PT -80016-A | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320PT80016A | Pair 10 | - | - |  | NON-IS | 320-P -80016 | - | Pressure Transmitter | PT | 2-Wire | 320-K-8061A/B HP NITROGEN COMPRESSOR DISCHARGE | AIR
Pressure | 320-UC-80001 |  | - | - | K-8061A/B HPN CMPR DISCH | 320-JE-0001 | - | PID-320800001 | - |  | 320-PT -80016-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 31 | Yes |  | 320 | - | 320PT80016B | Pair 11 | - | - |  | NON-IS | 320-P -80016 | - | Pressure Transmitter | PT | 2-Wire | 320-K-8061A/B HP NITROGEN COMPRESSOR DISCHARGE | AIR
Pressure | - |  | - | - | K-8061-A/B HPN DISCH | 320-JE-0001 | - | PID-320800001 | - |  | 320-PT -80017 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320PT80017 | Pair 12 | - | - |  | NON-IS | 320-P -80017 | - | Pressure Transmitter | PT | 2-Wire | 320-K-8061A/B HP NITROGEN DISCHARGE | AIR
Control Valve | - |  | - | - | K-8061-A/B HPN DISCH | 320-JE-0001 | - | PID-320800001 | - |  | 320-PV -80017-A | - | Modified |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 80 | - |  | 320 | 320-PV -80017 | 320PV80017A | Pair 13 | - | - |  | NON-IS | 320-P -80017 | - | Control Valve | PV | 2-Wire | 320-K-8061A/B HP NITROGEN DISCHARGE | AOR
Pressure | - |  | - | - | PLANT UNIT 1 LPN FRM OSBL | 320-JE-0001 | - | PID-320800001 | - |  | 320-PDT -80018 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320PDT80018 | Pair 14 | - | - |  | NON-IS | 320-PD-80018 | - | Diff.Pressure Transmitter | PDT | 2-Wire | PLANT UNIT 1 LPN FROM OSBL | AI
Temperature | - |  | - | - | PLANT UNIT 1 LPN FRM OSBL | 320-JE-0001 | - | PID-320800001 | - |  | 320-TT -80003 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320TT80003 | Pair 15 | - | - |  | NON-IS | 320-T -80003 | - | Temperature Transmitter | TT | 2-Wire | PLANT UNIT 1 LPN FROM OSBL | AI
Temperature | - |  | - | - | K-8061-A/B CWR | 320-JE-0001 | - | PID-320800001 | - |  | 320-TT -80005 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 30 | Yes |  | 320 | - | 320TT80005 | Pair 16 | - | - |  | NON-IS | 320-T -80005 | - | Temperature Transmitter | TT | 2-Wire | 320-K-8061A/B CWR | AI
Temperature | - |  | - | - | A-8063 VENT STM COND IN | 320-JE-0001 | - | PID-320803002 | - |  | 320-TT -83004 | - | Modified |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 0 | Yes |  | 320 | - | 320TT83004 | Pair 18 | - | - |  | NON-IS | 320-T -83004 | - | Temperature Transmitter | TT | 2-Wire | 320-A-8063 VENT STEAM CONDENSER INLET | AI
General | 320-UC-83061 |  | - | - | G-8062-B CLN CNDS SUCT | 320-JE-0001 | - | PID-320803003 | - |  | 320-XLS -83013-AO | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 31 | - |  | 320 | - | 320XLS83013AO | Pair 19 | - | NO |  | NON-IS | 320-X -83013 | - | Position Limit Switch | XLS | Voltfree-contact | 320-G-8062-B CLEAN CONDENSATE SUCTION | DIR
General | 320-UC-83061 |  | - | - | G-8062-B SSC SUCT | 320-JE-0001 | - | PID-320803003 | - |  | 320-XLS -83013-BO | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0001 | 31 | - |  | 320 | - | 320XLS83013BO | Pair 20 | - | NO |  | NON-IS | 320-X -83013 | - | Position Limit Switch | XLS | Voltfree-contact | 320-G-8062-B SUSPECT CONDENSATE SUCTION | DIR
Flow | - |  | - | - | G-8062-A/B CLN CNDS OUT | 320-JE-0004 | - | PID-320803003 | - |  | 320-FT -83010 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320FT83010 | Pair 1 | - | - |  | NON-IS | 320-F -83010 | - | dP Flow Transmitter | FT | 2-Wire | 320-G-8062-A/B CLEAN CONDENSATE OUTLET | AIR
Level | - | CONDENSATE KNOCK OUT DRUM | - | - | D-8062 CNDS KOD | 320-JE-0004 | - | PID-320803002 | 320-D-8062 |  | 320-LT -83005 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | Yes |  | 320 | - | 320LT83005 | Pair 2 | - | - |  | NON-IS | 320-L -83005 | B | dP Level Transmitter with seal | LT | 2-Wire | 320-D-8062 CONDENSATE KNOCK OUT DRUM | AI
Control Valve | - |  | - | - | D-8068 MP CNDS KO DRM | 320-JE-0004 | - | PID-320803001 | - |  | 320-LV -83006 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | - |  | 320 | - | 320LV83006 | Pair 3 | - | - |  | NON-IS | 320-L -83006 | - | Control Valve | LV | 2-Wire | 320-D-8068 MP CONDENSATE KO DRUM | AOR
Level | - | MP CONDENSATE K.O DRUM | - | - | D-8068 MP CNDS KO DRM | 320-JE-0004 | - | PID-320803001 | 320-D-8068 |  | 320-LT -83008 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | Yes |  | 320 | - | 320LT83008 | Pair 4 | - | - |  | NON-IS | 320-L -83008 | B-ALARM | dP Level Transmitter with seal | LT | 2-Wire | 320-D-8068 MP CONDENSATE KO DRUM | AI
Pressure | 320-UC-20011 |  | - | - | D-2020 H2 TO R-4101/4201 | 320-JE-0004 | - | PID-320200103 | - |  | 320-PT -20142-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 31 | Yes |  | 320 | - | 320PT20142B | Pair 5 | - | - |  | NON-IS | 320-P -20142 | B | Pressure Transmitter with Seal | PT | 2-Wire | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | AIR
Pressure | - |  | - | - | D-2020 H2 TO R-4101/4201 | 320-JE-0004 | - | PID-320200103 | - |  | 320-PT -20143-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 31 | Yes |  | 320 | - | 320PT20143B | Pair 6 | - | - |  | NON-IS | 320-P -20143 | - | Pressure Transmitter with Seal | PT | 2-Wire | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | AIR
Control Valve | - |  | - | - | D-2020 H2 TO R-4101/4201 | 320-JE-0004 | - | PID-320200103 | - |  | 320-PV -20143-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 81 | - |  | 320 | - | 320PV20143B | Pair 7 | - | - |  | NON-IS | 320-P -20143 | B | Control Valve | PV | 2-Wire | HYDRGEN FROM 320-D-2020 HYDROGEN COMPRESSOR DISCHARGE DRUM TO REACTOR 320-R-4101/4201 | AOR
Control Valve | - |  | - | - | REG RTRN TO A-2062 | 320-JE-0004 | - | PID-320200601 | - |  | 320-PV -20648 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 80 | - |  | 320 | - | 320PV20648 | Pair 8 | - | - |  | NON-IS | 320-P -20648 | - | Control Valve | PV | 2-Wire | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | AOR
Pressure | - |  | - | - | REG RTRN TO A-2062 | 320-JE-0004 | - | PID-320200601 | - |  | 320-PT -20657 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320PT20657 | Pair 9 | 320-F-2011 | - |  | NON-IS | 320-P -20657 | B-ALARM | Pressure Transmitter | PT | 2-Wire | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | AI
Pressure | - |  | - | - | D-8062 CNDS KOD | 320-JE-0004 | - | PID-320803002 | - |  | 320-PT -83001 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320PT83001 | Pair 10 | - | - |  | NON-IS | 320-P -83001 | - | Pressure Transmitter | PT | 2-Wire | 320-D-8062 CONDENSATE KNOCK OUT DRUM | AIR
Pressure | - |  | - | - | G-8068-B DIAPHRAGM FAIL | 320-JE-0004 | - | PID-320803004 | 320-G-8068-B |  | 320-PT -83008 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | Yes |  | 320 | - | 320PT83008 | Pair 11 | PKG-034001 | - |  | NON-IS | 320-P -83008 | B | Pressure Transmitter | PT | 2-Wire | 320-G-8068-B MP CONDENSATE PUMP DIAPHRAGM FAILURE | AI
Temperature | - |  | - | - | E-2002 ETH TO FLR | 320-JE-0004 | - | PID-320200401 | - |  | 320-TT -20488 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320TT20488 | Pair 12 | - | - |  | NON-IS | 320-T -20488 | - | Temperature Transmitter | TT | 2-Wire | ETHYLENE FROM 320-E-2002 HEATER TO FLARE | AI
Temperature | - |  | - | - | REG RTRN TO A-2062 | 320-JE-0004 | - | PID-320200601 | - |  | 320-TT -20660 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320TT20660 | Pair 13 | - | - |  | NON-IS | 320-T -20660 | - | Temperature Transmitter | TT | 2-Wire | REGEN RETURN AND COOLING NITROGEN RETURN TO 320-A-2062 VENT COOLER | AI
Temperature | - |  | - | - | A-2062 REG RTRN TO FLR | 320-JE-0004 | - | PID-320200601 | - |  | 320-TT -20662 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | - | 320TT20662 | Pair 14 | - | - |  | NON-IS | 320-T -20662 | - | Temperature Transmitter | TT | 2-Wire | REGEN RETURN AND COOLING NITROGEN RETURN TO FLARE FROM 320-A-2062 VENT COOLER | AI
Temperature | - |  | - | - | A-8063 VENT STM COND OUT | 320-JE-0004 | - | PID-320803002 | - |  | 320-TT -83007 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | Yes |  | 320 | - | 320TT83007 | Pair 15 | - | - |  | NON-IS | 320-T -83007 | - | Temperature Transmitter | TT | 2-Wire | 320-A-8063 VENT STEAM CONDENSER OUTLET | AI
Temperature | - |  | - | - | A-8064 SS STM COND OUT | 320-JE-0004 | - | PID-320803005 | - |  | 320-TT -83052 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 0 | Yes |  | 320 | - | 320TT83052 | Pair 16 | - | - |  | NON-IS | 320-T -83052 | - | Temperature Transmitter | TT | 2-Wire | 320-A-8064 SUSPECT VENT STEAM CONDENSER OUTLET | AI
General | 320-UC-83061 |  | - | - | G-8062-B CLN CNDS/D-8062 | 320-JE-0004 | - | PID-320803003 | - |  | 320-XLS -83011-C | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | - |  | 320 | - | 320XLS83011C | Pair 17 | - | NO |  | NON-IS | 320-X -83011 | - | Position Limit Switch | XLS | Voltfree-contact | 320-G-8062-B CLEAN CONDENSATE TO 320-D-8062 | DIR
General | 320-UC-83061 |  | - | - | G-8062-B CLN CNDS/D-8062 | 320-JE-0004 | - | PID-320803003 | - |  | 320-XLS -83011-O | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 31 | - |  | 320 | - | 320XLS83011O | Pair 18 | - | NO |  | NON-IS | 320-X -83011 | - | Position Limit Switch | XLS | Voltfree-contact | 320-G-8062-B CLEAN CONDENSATE TO 320-D-8062 | DIR
Pressure | - |  | - | - | D-8002 FLR TO G-8002-B | 320-JE-0004 | - | PID-320806303 | - |  | 320-PDT -86352 | - | Modified |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0004 | 30 | Yes |  | 320 | 320-FT -20646-B | 320PDT86352 | Pair 19 | - | - |  | NON-IS | 320-PD-86352 | B | Diff. Pressure Transmitter with Seal | PDT | 2-Wire | D-8002 FLR TO G-8002-B | AI
Flow | - |  | - | - | G-4202 CLNT/E-4201A/B/C | 320-JE-0035 | - | PID-320402701 | - |  | 320-FT -42766 | - | New |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0035 | 30 | Yes |  | 320 | - | 320FT42766 | Pair 1 | - | - |  | NON-IS | 320-F -42766 | - | dP Flow Transmitter | FT | 2-Wire | 320-G-4202 COOLANT SUPPLY TO 320-E-4201A/B/C EXCHANGER | AIR
Temperature | - |  | - | - | CLNT SPLY TO R-4101 | 320-JE-0035 | - | PID-320401702 | - |  | 320-TT -41752-A | - | New |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0035 | 30 | Yes |  | 320 | - | 320TT41752A | Pair 2 | - | - |  | NON-IS | 320-T -41752 | - | Temperature Transmitter | TT | 2-Wire | COOLANT SUPPLY TO 320-R-4101 REACTOR A | AIR
Temperature | - |  | - | - | CLNT SPLY TO R-4201 | 320-JE-0035 | - | PID-320402702 | - |  | 320-TT -42753-A | - | New |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0035 | 30 | Yes |  | 320 | - | 320TT42753A | Pair 3 | - | - |  | NON-IS | 320-T -42753 | - | Temperature Transmitter | TT | 2-Wire | COOLANT SUPPLY TO 320-R-4201 REACTOR B | AIR
Temperature | - |  | - | - | DS-8211 MPS VENT TO ATM | 320-JE-0035 | - | PID-320802101 | - |  | 320-TT -82118 | - | New |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0035 | 0 | Yes |  | 320 | - | 320TT82118 | Pair 4 | - | - |  | NON-IS | 320-T -82118 | A | Temperature Transmitter | TT | 2-Wire | 320-DS-8211 MPS DESUPERHEATER VENT TO ATM | AI
Level | - | HEXENE TREATER | - | - | D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | 320-D-2034-A |  | 320-LT -20363 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320LT20363 | Pair 1 | - | - |  | NON-IS | 320-L -20363 | A | dP Level Transmitter with seal | LT | 2-Wire | 320-D-2034-A HEXENE TREATER | AI
Pressure | - |  | - | - | LPN TO D-2032 HXE SRG TK | 320-JE-0040 | - | PID-320200201 | - |  | 320-PT -20245 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 |  | Yes |  | 320 | - | 320PT20245 | Pair 2 | - | - |  | NON-IS | 320-P -20245 | - | Pressure Transmitter with Seal | PT | 2-Wire | LPN TO 320-D-2032 HEXENE SURGE TANK | AI
Pressure | - |  | - | - | E-5043 HXE TO D-2034-A/B | 320-JE-0040 | - | PID-320200301 | - |  | 320-PT -20301 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320PT20301 | Pair 3 | - | - |  | NON-IS | 320-P -20301 | A | Pressure Transmitter with Seal | PT | 2-Wire | HEXENE FROM 320-E-5043 SIDEDRAW CONDENSER TO 320-D-2034-A/B | AI
Temperature | 320-UC-20061 |  | - | - | D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20350 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20350 | Pair 4 | - | - |  | NON-IS | 320-T -20350 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER | AIR
Temperature | 320-UC-20061 |  | - | - | D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20351 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20351 | Pair 5 | - | - |  | NON-IS | 320-T -20351 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER | AIR
Temperature | - |  | - | - | D-2034-A HXE TRT OUT | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20361 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20361 | Pair 6 | - | - |  | NON-IS | 320-T -20361 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER OUTLET | AI
Temperature | 320-UC-20061 |  | - | - | D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20362 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20362 | Pair 7 | - | - |  | NON-IS | 320-T -20362 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER | AIR
Temperature | 320-UC-20061 |  | - | - | D-2034-A HXE TRT BTM | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20365 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20365 | Pair 8 | - | - |  | NON-IS | 320-T -20365 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER BOTTOM | AIR
Temperature | 320-UC-20061 |  | - | - | D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-TT -20388 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | Yes |  | 320 | - | 320TT20388 | Pair 9 | - | - |  | NON-IS | 320-T -20388 | A | Temperature Transmitter | TT | 2-Wire | 320-D-2034-A HEXENE TREATER | AIR
General | 320-UC-20061 |  | - | - | LPN TO D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20301-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | - |  | 320 | - | 320XLS20301C | Pair 10 | - | NO |  | NON-IS | 320-X -20301 | A | Position Limit Switch | XLS | Voltfree-contact | LOW PRESSURE NITROGEN TO 320-D-2034-A HEXENE TREATER | DIR
General | 320-UC-20061 |  | - | - | LPN TO D-2034-A HXE TRT | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20301-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 31 | - |  | 320 | - | 320XLS20301O | Pair 11 | - | NO |  | NON-IS | 320-X -20301 | A | Position Limit Switch | XLS | Voltfree-contact | LOW PRESSURE NITROGEN TO 320-D-2034-A HEXENE TREATER | DIR
General | 320-UC-20061 |  | - | - | REG & CLG N2 TO D-2034-A | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20302-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | - |  | 320 | - | 320XLS20302C | Pair 12 | - | NO |  | NON-IS | 320-X -20302 | A | Position Limit Switch | XLS | Voltfree-contact | REGEN SUPPLY & COOLING NITROGEN SUPPLY TO 320-D-2034-A HEXEN TREATER | DIR
General | 320-UC-20061 |  | - | - | REG & CLG N2 TO D-2034-A | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20302-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 31 | - |  | 320 | - | 320XLS20302O | Pair 13 | - | NO |  | NON-IS | 320-X -20302 | A | Position Limit Switch | XLS | Voltfree-contact | REGEN SUPPLY & COOLING NITROGEN SUPPLY TO 320-D-2034-A HEXEN TREATER | DIR
General | 320-UC-20061 |  | - | - | D-2034A REG RTRN TO FLR | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20305-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | - |  | 320 | - | 320XLS20305C | Pair 14 | - | NO |  | NON-IS | 320-X -20305 | A | Position Limit Switch | XLS | Voltfree-contact | 320-D-2034-A REGEN RETURN & COOLING NITROGEN RETURN TO FLARE HEADER | DIR
General | 320-UC-20061 |  | - | - | D-2034A REG RTRN TO FLR | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20305-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 31 | - |  | 320 | - | 320XLS20305O | Pair 15 | - | NO |  | NON-IS | 320-X -20305 | A | Position Limit Switch | XLS | Voltfree-contact | 320-D-2034-A REGEN RETURN & COOLING NITROGEN RETURN TO FLARE HEADER | DIR
General | 320-UC-20061 |  | - | - | HXE TO D-2032 SRG VESL | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20306-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | - |  | 320 | - | 320XLS20306C | Pair 16 | - | NO |  | NON-IS | 320-X -20306 | A | Position Limit Switch | XLS | Voltfree-contact | HEXENE TO 320-D-2032 HEXENE SURGE VESSEL | DIR
General | 320-UC-20061 |  | - | - | HXE TO D-2032 SRG VESL | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20306-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 31 | - |  | 320 | - | 320XLS20306O | Pair 17 | - | NO |  | NON-IS | 320-X -20306 | A | Position Limit Switch | XLS | Voltfree-contact | HEXENE TO 320-D-2032 HEXENE SURGE VESSEL | DIR
General | 320-UC-20061 |  | - | HEXENE TO 320-S-2034 HEXENE FILTER | D-2034-A HXE TO S-2034 | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20309-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 30 | - |  | 320 | - | 320XLS20309C | Pair 18 | - | NO |  | NON-IS | 320-X -20309 | A | Position Limit Switch | XLS | Voltfree-contact | HEXENE TO 320-S-2034 HEXENE FILTER FROM 320-D-2034-A | DIR
General | 320-UC-20061 |  | - | HEXENE TO 320-S-2034 HEXENE FILTER | D-2034-A HXE TO S-2034 | 320-JE-0040 | - | PID-320200301 | - |  | 320-XLS -20309-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0040 | 31 | - |  | 320 | - | 320XLS20309O | Pair 19 | - | NO |  | NON-IS | 320-X -20309 | A | Position Limit Switch | XLS | Voltfree-contact | HEXENE TO 320-S-2034 HEXENE FILTER FROM 320-D-2034-A | DIR
Temperature | - |  | - | - | G-2032B HXE / E-2033 CLR | 320-JE-0045 | - | PID-320200202 | - |  | 320-TT -20205 | - | New |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 30 | Yes |  | 320 | - | 320TT20205 | Pair 1 | - | - |  | NON-IS | 320-T -20205 | - | Temperature Transmitter | TT | 2-Wire | HEXENE FROM 320-G-2032-B DISCHARGE TO 320-E-2033 HEXENE COOLER | AI
Level | - | HEXENE TREATER | - | - | D-2034-B HXE TRAETER | 320-JE-0045 | - | PID-320200302 | 320-D-2034-B |  | 320-LT -20371 | - | New |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 30 | Yes |  | 320 | - | 320LT20371 | Pair 3 | - | - |  | NON-IS | 320-L -20371 | B | dP Level Transmitter with seal | LT | 2-Wire | 320-D-2034-B HEXENE TRAETER | AI
Pressure | - |  | - | - | REG SPLY TO D-4143-B | 320-JE-0045 | - | PID-320400202 | - |  | 320-PT -40211-A | - | New |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 30 | Yes |  | 320 | - | 320PT40211A | Pair 4 | - | - |  | NON-IS | 320-P -40211 | B | Pressure Transmitter with Seal | PT | 2-Wire | REGEN SPLY TO 320-D-4143-B RECYCLE ISOBUTANE TREATER INLET/OUTLET | AI
Pressure | - |  | - | - | REG SPLY TO D-4143-B | 320-JE-0045 | - | PID-320400202 | - |  | 320-PT -40211-B | - | New |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 31 | Yes |  | 320 | - | 320PT40211B | Pair 5 | - | - |  | NON-IS | 320-P -40211 | B | Pressure Transmitter with Seal | PT | 2-Wire | REGEN SPLY TO 320-D-4143-B RECYCLE ISOBUTANE TREATER INLET/OUTLET | AI
Pressure | - |  | - | - | S-4243 RCYCL IBT FLTR | 320-JE-0045 | - | PID-320400203 | - |  | 320-PDT -40227 | - | New |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 30 | Yes |  | 320 | - | 320PDT40227 | Pair 6 | - | - |  | NON-IS | 320-PD-40227 | - | Diff.Pressure Transmitter with Seal | PDT | 2-Wire | 320-4243 RECYCLE ISOBTANE FILTER PRESSURE | AI
General | 320-UC-20070 |  | - | - | HXE FRM G-2032-B DISCH | 320-JE-0045 | - | PID-320200202 | - |  | 320-XHSC -20202-L | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 |  | - |  | 320 | - | 320XHSC20202L | Pair 7 | - | NO |  | NON-IS | 320-X -20202 | B | Hand Switch | XHSC | Voltfree-contact | HEXENE FROM 320-G-2032-B DISCHARGE | DIR
General | 320-UC-20070 |  | - | - | HXE FRM G-2032-B DISCH | 320-JE-0045 | - | PID-320200202 | - |  | 320-XHSO -20202-L | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 |  | - |  | 320 | - | 320XHSO20202L | Pair 8 | - | NO |  | NON-IS | 320-X -20202 | B | Hand Switch | XHSO | Voltfree-contact | HEXENE FROM 320-G-2032-B DISCHARGE | DIR
General | - |  | - | TYPICAL E2 | HXE FRM G-2032-B DISCH | 320-JE-0045 | - | PID-320200202 | - |  | 320-XLS -20202-C | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 30 | - |  | 320 | - | 320XLS20202C | Pair 9 | - | NO |  | NON-IS | 320-X -20202 | B | Position Limit Switch | XLS | Voltfree-contact | HEXENE FROM 320-G-2032-B DISCHARGE | DI
General | - |  | - | TYPICAL E2 | HXE FRM G-2032-B DISCH | 320-JE-0045 | - | PID-320200202 | - |  | 320-XLS -20202-O | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0045 | 31 | - |  | 320 | - | 320XLS20202O | Pair 10 | - | NO |  | NON-IS | 320-X -20202 | B | Position Limit Switch | XLS | Voltfree-contact | HEXENE FROM 320-G-2032-B DISCHARGE | DI
Control Valve | - |  | - | - | RIB FLUSH TO R-4201 L8 | 320-JE-0083 | - | PID-320402401 | - |  | 320-FV -42420 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 80 | - |  | 320 | - | 320FV42420 | Pair 1 | - | - |  | NON-IS | 320-F -42420 | - | Control Valve | FV | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-R-4201 LOOP REACTOR B LEG .8 | AOR
Flow | - |  | - | - | OFI TO X4201 REAC B CIRC | 320-JE-0083 | - | PID-320402801 | - |  | 320-FT -42889-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 31 | Yes |  | 320 | - | 320FT42889B | Pair 2 | - | - |  | NON-IS | 320-F -42889 | B-ALARM | dP Flow Transmitter with seal | FT | 2-Wire | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | AI
Control Valve | - |  | - | - | OFI TO X4201 REAC B CIRC | 320-JE-0083 | - | PID-320402801 | - |  | 320-FV -42889 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 80 | - |  | 320 | - | 320FV42889 | Pair 3 | - | - |  | NON-IS | 320-F -42889 | - | Control Valve | FV | 2-Wire | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | AOR
Pressure | - |  | - | - | OFI TO X4201 REAC B CIRC | 320-JE-0083 | - | PID-320402801 | - |  | 320-PT -42890 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | Yes |  | 320 | - | 320PT42890 | Pair 4 | - | - |  | NON-IS | 320-P -42890 | - | Pressure Transmitter with Seal | PT | 2-Wire | OLEFIN FREE ISOBUTANE TO 320-X-4201 REACTOR B CIRCULATION PUMP PACKAGE | AI
Temperature | - |  | - | - | R-4201 REAC B LEG .7 | 320-JE-0083 | - | PID-320402401 | - |  | 320-TT -42409-A | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | Yes |  | 320 | - | 320TT42409A | Pair 5 | - | - |  | NON-IS | 320-T -42409 | - | Temperature Transmitter | TT | 2-Wire | 320-R-4201 LOOP REACTOR B LEG .7 | AI
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO R-4201-A | 320-JE-0083 | - | PID-320402301 | - |  | 320-XLS -42318-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | - |  | 320 | - | 320XLS42318C | Pair 6 | - | NO |  | NON-IS | 320-X -42318 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-A FLASHLINE HEATER | DIR
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO R-4201-A | 320-JE-0083 | - | PID-320402301 | - |  | 320-XLS -42318-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 31 | - |  | 320 | - | 320XLS42318O | Pair 7 | - | NO |  | NON-IS | 320-X -42318 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-A FLASHLINE HEATER | DIR
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO R-4201-B | 320-JE-0083 | - | PID-320402301 | - |  | 320-XLS -42319-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | - |  | 320 | - | 320XLS42319C | Pair 8 | - | NO |  | NON-IS | 320-X -42319 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | DIR
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO R-4201-B | 320-JE-0083 | - | PID-320402301 | - |  | 320-XLS -42319-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 31 | - |  | 320 | - | 320XLS42319O | Pair 9 | - | NO |  | NON-IS | 320-X -42319 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | DIR
General | - |  | - | TYPICAL H2 | RIB FLUSH TO R-4201-B | 320-JE-0083 | - | PID-320402301 | - |  | 320-XPT -42319 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 32 | Yes |  | 320 | - | 320XPT42319 | Pair 10 | - | - |  | NON-IS | 320-X -42319 | - | Pressure Transmitter | XPT | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-R-4201-B FLASHLINE HEATER | AI
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-F | 320-JE-0083 | - | PID-320402401 | - |  | 320-XLS -42418-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | - |  | 320 | - | 320XLS42418C | Pair 11 | - | NO |  | NON-IS | 320-X -42418 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | DIR
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-F | 320-JE-0083 | - | PID-320402401 | - |  | 320-XLS -42418-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 31 | - |  | 320 | - | 320XLS42418O | Pair 12 | - | NO |  | NON-IS | 320-X -42418 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | DIR
General | - |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-F | 320-JE-0083 | - | PID-320402401 | - |  | 320-XPT -42418 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 32 | Yes |  | 320 | - | 320XPT42418 | Pair 13 | - | - |  | NON-IS | 320-X -42418 | - | Pressure Transmitter | XPT | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-F FLASHLINE HEATER | AI
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-E | 320-JE-0083 | - | PID-320402401 | - |  | 320-XLS -42419-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 30 | - |  | 320 | - | 320XLS42419C | Pair 14 | - | NO |  | NON-IS | 320-X -42419 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | DIR
General | 320-UC-42011 |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-E | 320-JE-0083 | - | PID-320402401 | - |  | 320-XLS -42419-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 31 | - |  | 320 | - | 320XLS42419O | Pair 15 | - | NO |  | NON-IS | 320-X -42419 | - | Position Limit Switch | XLS | Voltfree-contact | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | DIR
General | - |  | - | TYPICAL H2 | RIB FLUSH TO E-4221-E | 320-JE-0083 | - | PID-320402401 | - |  | 320-XPT -42419 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 32 | Yes |  | 320 | - | 320XPT42419 | Pair 16 | - | - |  | NON-IS | 320-X -42419 | - | Pressure Transmitter | XPT | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-E FLASHLINE HEATER | AI
Pressure | - |  | - | TYPICAL L2 | R-4201 PSLY TO D-4023 | 320-JE-0083 | - | PID-320402301 | - |  | 320-ZPT -42310 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 35 | Yes |  | 320 | - | 320ZPT42310 | Pair 17 | - | - |  | NON-IS | 320-Z -42310 | - | Pressure Transmitter | ZPT | 2-Wire | 320-R-4201 POLYMER SLURRY TO 320-D-4023 REACTOR DUMP VESSEL | AI
Pressure | - |  | - | TYPICAL L2 | R-4201 L8 PSLY/D-40232 | 320-JE-0083 | - | PID-320402401 | - |  | 320-ZPT -42410 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0083 | 35 | Yes |  | 320 | - | 320ZPT42410 | Pair 18 | - | - |  | NON-IS | 320-Z -42410 | - | Pressure Transmitter | ZPT | 2-Wire | 320-R-4201 LEG.8 POLYMER SLURRY TO 320-D-40232 REACTOR DUMP VESSEL | AI
General |  |  | - | - | R-4101 REAC A LEG.6 | 320-JE-0083 | - | PID-320401301 | - |  | 320-AXS -42250-A | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 320-CE-0083 | 30 | - |  | 320 | - | 320AXS42250A | Pair 19 | - | NC |  | NON-IS | 320-A -42250 | - | General Fault Switch | AXS | Voltfree-contact | 320-R-4101 LOOP REACTOR A LEG.6 | DI
Flow | - |  | - | - | RIB TO C-5041 DEHEX COL | 320-JE-0087 | - | PID-320402001 | - |  | 320-FT -42044 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | 230VAC | L | 320-CE-0087 | 30 | No |  | 320 | - | 320FT42044 | Pair 1 | - | - |  | NON-IS | 320-F -42044 | - | Coriolis Meter | FT | 4-Wire | RECYCLE ISOBUTANE TO 320-C-5041 DEHEX COLUMN | AIR
Control Valve | - |  | - | - | RIB TO C-5041 DEHEX COL | 320-JE-0087 | - | PID-320402001 | - |  | 320-FV -42044 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 80 | - |  | 320 | - | 320FV42044 | Pair 2 | - | - |  | NON-IS | 320-F -42044 | - | Control Valve | FV | 2-Wire | RECYCLE ISOBUTANE TO 320-C-5041 DEHEX COLUMN | AOR
Flow | - |  | - | - | TRTD RIB TO R-4201 HDR | 320-JE-0087 | - | PID-320402001 | - |  | 320-FT -42048 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | 230VAC | L | 320-CE-0087 | 30 | No |  | 320 | - | 320FT42048 | Pair 3 | - | - |  | NON-IS | 320-F -42048 | A-CONTROL | Coriolis Meter | FT | 4-Wire | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | AIR
Control Valve | - |  | - | - | TRTD RIB TO R-4201 HDR | 320-JE-0087 | - | PID-320402001 | - |  | 320-FV -42048 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 80 | - |  | 320 | - | 320FV42048 | Pair 4 | - | - |  | NON-IS | 320-F -42048 | - | Control Valve | FV | 2-Wire | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | AOR
Flow | - |  | - | - | HXE TRTD FRM G-2032-A/B | 320-JE-0087 | - | PID-320402002 | - |  | 320-FT -42049-A | - | Modified |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | 230VAC | L | 320-CE-0087 | 30 | No |  | 320 | 320-FT -42049 | 320FT42049A | Pair 5 | - | - |  | NON-IS | 320-F -42049 | - | Coriolis Meter | FT | 4-Wire | HEXENE TREATED FROM HEXENE FEED PUMPS 320-G-2032-A/B | AIR
Control Valve | - |  | - | - | HXE TRTD FRM G-2032-A/B | 320-JE-0087 | - | PID-320402002 | - |  | 320-FV -42049-A | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 80 | - |  | 320 | - | 320FV42049A | Pair 6 | - | - |  | NON-IS | 320-F -42049 | - | Control Valve | FV | 2-Wire | HEXENE TREATED FROM HEXENE FEED PUMPS 320-G-2032-A/B | AOR
Flow | - |  | - | - | S2011 TRTD ETH/R4201 L2 | 320-JE-0087 | - | PID-320402002 | - |  | 320-FT -42058 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | 230VAC | L | 320-CE-0087 | 30 | No |  | 320 | - | 320FT42058 | Pair 7 | - | - |  | NON-IS | 320-F -42058 | A-CONTROL | Coriolis Meter | FT | 4-Wire | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | AIR
Flow | - |  | - | - | RIB FLUSH TO R-4201 TOP | 320-JE-0087 | - | PID-320402001 | - |  | 320-FT -42060 | - | Modified |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | 230VAC | L | 320-CE-0087 | 30 | No |  | 320 | - | 320FT42060 | Pair 8 | - | - |  | NON-IS | 320-F -42060 | - | Coriolis Meter | FT | 4-Wire | RECYCLE ISOBUTANE FLUSH TO 320-R-4201 REACTOR TOP | AIR
Pressure | - |  | - | - | TRTD RIB TO R-4201 | 320-JE-0087 | - | PID-320402001 | - |  | 320-PT -42047 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 0 | Yes |  | 320 | - | 320PT42047 | Pair 9 | - | - |  | NON-IS | 320-P -42047 | - | Pressure Transmitter with Seal | PT | 2-Wire | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 | AI
Pressure | - |  | - | - | S2011 TRTD ETH/R4201 L2 | 320-JE-0087 | - | PID-320402002 | - |  | 320-PT -42055 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 0 | Yes |  | 320 | - | 320PT42055 | Pair 10 | - | - |  | NON-IS | 320-P -42055 | - | Pressure Transmitter with Seal | PT | 2-Wire | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | AI
Pressure | - |  | - | - | TRTD RIB TO R-4201 HDR | 320-JE-0087 | - | PID-320402001 | - |  | 320-PT -42062-A | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 43 | Yes |  | 320 | - | 320PT42062A | Pair 11 | - | - |  | NON-IS | 320-P -42062 | - | Pressure Transmitter with Seal | PT | 2-Wire | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | AI
Pressure | - |  | - | - | TRTD RIB TO R-4201 HDR | 320-JE-0087 | - | PID-320402001 | - |  | 320-PT -42062-B | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 31 | Yes |  | 320 | - | 320PT42062B | Pair 12 | - | - |  | NON-IS | 320-P -42062 | - | Pressure Transmitter with Seal | PT | 2-Wire | TREATED RECYCLE ISOBUTANE TO REACTOR 320-R-4201 FEED HEADER | AI
Control Valve | - |  | - | - | RIB FLUSH TO E-4221-B | 320-JE-0087 | - | PID-320402201 | - |  | 320-PV -42207 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 80 | - |  | 320 | - | 320PV42207 | Pair 13 | - | - |  | NON-IS | 320-P -42207 | - | Control Valve | PV | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-B FLASHLINE HEATER | AOR
General | 320-UC-42011 |  | - | - | RIB FLUSH TO E-4221-B | 320-JE-0087 | - | PID-320402201 | - |  | 320-PZT -42207 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 30 | Yes |  | 320 | - | 320PZT42207 | Pair 14 | - | - |  | NON-IS | 320-P -42207 | - | Position Transmitter | PZT | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-B FLASHLINE HEATER | AIR
Control Valve | - |  | - | - | RIB FLUSH TO E-4221-A | 320-JE-0087 | - | PID-320402201 | - |  | 320-PV -42209 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 80 | - |  | 320 | - | 320PV42209 | Pair 15 | - | - |  | NON-IS | 320-P -42209 | - | Control Valve | PV | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-A FLASHLINE HEATER | AOR
General | 320-UC-42011 |  | - | - | RIB FLUSH TO E-4221-A | 320-JE-0087 | - | PID-320402201 | - |  | 320-PZT -42209-C | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 30 | Yes |  | 320 | - | 320PZT42209C | Pair 16 | - | - |  | NON-IS | 320-P -42209 | - | Position Transmitter | PZT | 2-Wire | RECYCLE ISOBUTANE FLUSH TO 320-E-4221-A FLASHLINE HEATER | AIR
Pressure | - |  | - | - | S2011 TRTD ETH/R4201 L2 | 320-JE-0087 | - | PID-320402002 | - |  | 320-PDT -42054 | - | New |  | DCS | 4-20 ma HART | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 0 | Yes |  | 320 | - | 320PDT42054 | Pair 17 | - | - |  | NON-IS | 320-PD-42054 | - | Diff.Pressure Transmitter with Seal | PDT | 2-Wire | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | AI
General | - |  | - | TYPICAL A2 | S2011 TRTD ETH/R4201 L2 | 320-JE-0087 | - | PID-320402002 | - |  | 320-ZLS -42050-C | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 30 | - |  | 320 | - | 320ZLS42050C | Pair 18 | - | NO |  | NON-IS | 320-Z -42050 | - | Position Limit Switch | ZLS | Voltfree-contact | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | DI
General | - |  | - | TYPICAL A2 | S2011 TRTD ETH/R4201 L2 | 320-JE-0087 | - | PID-320402002 | - |  | 320-ZLS -42050-O | - | New |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 320-CE-0087 | 31 | - |  | 320 | - | 320ZLS42050O | Pair 19 | - | NO |  | NON-IS | 320-Z -42050 | - | Position Limit Switch | ZLS | Voltfree-contact | TREATED ETHYLENE FROM 320-S-2011 FILTER TO 320-R-4201 LEG.N. 2 | DI
Control Valve | 320-UC-20070 |  | - | TYPICAL E2 | HXE FRM G-2032-B DISCH | 320-JS-0005 | - | PID-320200202 | - |  | 320-XYV -20202 | - | New |  | DCS | - | 12PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0005 | 70 | - |  | 320 | - | 320XYV20202 | Pair 2 | - | - |  | NON-IS | 320-X -20202 | B | Solenoid Valve | XYV | Volt-contact | HEXENE FROM 320-G-2032-B DISCHARGE | DOR
Control Valve | 320-UC-40015 |  | - | TYPICAL E2 | LPN TO D-4143-A OFI TRT | 320-JS-0005 | - | PID-320400001 | - |  | 320-XYV -40030 | - | New |  | DCS | - | 12PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0005 | 0 | - |  | 320 | - | 320XYV40030 | Pair 3 | - | - |  | NON-IS | 320-X -40030 | - | Solenoid Valve | XYV | Volt-contact | LPN TO 320-D-4143-AOLEFINE FREE ISOBUTANE TREATER | DOR
Control Valve | 320-UC-41050 |  | - | TYPICAL E2 | G-4142 B OFI PMP DISCH | 320-JS-0005 | - | PID-320400102 | - |  | 320-XYV -40102 | - | New |  | DCS | - | 12PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0005 | 70 | - |  | 320 | - | 320XYV40102 | Pair 4 | - | - |  | NON-IS | 320-X -40102 | B | Solenoid Valve | XYV | Volt-contact | 320-G-4142 B OLEFIN FREE ISOBUTANE PUMP DISCHARGE | DOR
Control Valve | 320-UC-42050 |  | - | TYPICAL E2 | G-4242-B RIB DISCH | 320-JS-0005 | - | PID-320400302 | - |  | 320-XYV -40301 | - | New |  | DCS | - | 12PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0005 | 70 | - |  | 320 | - | 320XYV40301 | Pair 5 | - | - |  | NON-IS | 320-X -40301 | B | Solenoid Valve | XYV | Volt-contact | 320-G-4242-B RECYCLE ISOBUTANE PUMP DISCHARGE | DOR
Control Valve | 320-UC-40033 |  | - | TYPICAL E2 | OFI TO D-4242 RIB VESL | 320-JS-0005 | - | PID-320400301 | - |  | 320-XYV -40345 | - | New |  | DCS | - | 12PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0005 | 70 | - |  | 320 | - | 320XYV40345 | Pair 6 | - | - |  | NON-IS | 320-X -40345 | - | Solenoid Valve | XYV | Volt-contact | OLEFIN FREE ISOBUTANE TO 320-D-4242 RECYCLE ISOBUTANE VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL F2 | R-4101 VENT TO D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-XYV -40529-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV40529C | Pair 1 | - | - |  | NON-IS | 320-X -40529 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4101 VENT TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL F2 | R-4101 VENT TO D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-XYV -40529-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV40529O | Pair 2 | - | - |  | NON-IS | 320-X -40529 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4101 VENT TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL F2 | R-4201 VENT TO D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-XYV -40551-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV40551C | Pair 3 | - | - |  | NON-IS | 320-X -40551 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4201 VENT TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL F2 | R-4201 VENT TO D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-XYV -40551-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV40551O | Pair 4 | - | - |  | NON-IS | 320-X -40551 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4201 VENT TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221-A FLASHLINE HTR | 320-JS-0008 | - | PID-320403301 | - |  | 320-XYV -42901-AC | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42901AC | Pair 5 | - | - |  | NON-IS | 320-X -42901 | A | Solenoid Valve | XYV | Volt-contact | 320-E-4221A FLASH LINE HEATER A | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221-A FLASHLINE HTR | 320-JS-0008 | - | PID-320403301 | - |  | 320-XYV -42901-AO | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42901AO | Pair 6 | - | - |  | NON-IS | 320-X -42901 | A | Solenoid Valve | XYV | Volt-contact | 320-E-4221A FLASH LINE HEATER A | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221C FLASH LINE HTR C | 320-JS-0008 | - | PID-320403303 | - |  | 320-XYV -42903-AC | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42903AC | Pair 7 | - | - |  | NON-IS | 320-X -42903 | C | Solenoid Valve | XYV | Volt-contact | 320-E-4221C FLASH LINE HEATER C | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221C FLASH LINE HTR C | 320-JS-0008 | - | PID-320403303 | - |  | 320-XYV -42903-AO | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42903AO | Pair 8 | - | - |  | NON-IS | 320-X -42903 | C | Solenoid Valve | XYV | Volt-contact | 320-E-4221C FLASH LINE HEATER C | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221-E FLASHLINE HTR | 320-JS-0008 | - | PID-320403305 | - |  | 320-XYV -42905-AC | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42905AC | Pair 9 | - | - |  | NON-IS | 320-X -42905 | E | Solenoid Valve | XYV | Volt-contact | 320-E-4221E FLASH LINE HEATER E | DOR
Control Valve | 320-UC-42091 |  | - | TYPICAL F2 | E-4221-E FLASHLINE HTR | 320-JS-0008 | - | PID-320403305 | - |  | 320-XYV -42905-AO | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320XYV42905AO | Pair 10 | - | - |  | NON-IS | 320-X -42905 | E | Solenoid Valve | XYV | Volt-contact | 320-E-4221E FLASH LINE HEATER E | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4101 L7&8 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40511-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40511C | Pair 11 | - | - |  | NON-IS | 320-Z -40511 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 7&8 320-R-4101 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4101 L7&8 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40511-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40511O | Pair 12 | - | - |  | NON-IS | 320-Z -40511 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 7&8 320-R-4101 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L7&8 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40512-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40512C | Pair 13 | - | - |  | NON-IS | 320-Z -40512 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 7&8 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L7&8 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40512-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40512O | Pair 14 | - | - |  | NON-IS | 320-Z -40512 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 7&8 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L5&6 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40525-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40525C | Pair 15 | - | - |  | NON-IS | 320-Z -40525 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 5&6 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L5&6 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40525-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40525O | Pair 16 | - | - |  | NON-IS | 320-Z -40525 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 5&6 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L1&2 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40526-C | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40526C | Pair 17 | - | - |  | NON-IS | 320-Z -40526 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 1&2 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-40051 |  | - | TYPICAL L2 | R-4201 L1&2 PSLY/D-4023 | 320-JS-0008 | - | PID-320400501 | - |  | 320-ZYV -40526-O | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0008 |  | - |  | 320 | - | 320ZYV40526O | Pair 18 | - | - |  | NON-IS | 320-Z -40526 | - | Solenoid Valve | ZYV | Volt-contact | POLYMER SLURRY FROM LEG 1&2 320-R-4201 TO 320-D-4023 REACTOR DUMP VESSEL | DOR
Control Valve | 320-UC-42031 |  | - | TYPICAL E2 | VENT TO DMP VESL | 320-JS-0022 | - | PID-320402101 | - |  | 320-XYV -42170 | - | New |  | DCS | - | 06PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0022 | 70 | - |  | 320 | - | 320XYV42170 | Pair 1 | - | - |  | NON-IS | 320-X -42170 | - | Solenoid Valve | XYV | Volt-contact | VENT TO DUMP VESSEL | DOR
Control Valve | 320-UC-42031 |  | - | TYPICAL E2 | R-4201 RIB FLUSH/D-4023 | 320-JS-0022 | - | PID-320402201 | - |  | 320-XYV -42288 | - | New |  | DCS | - | 06PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0022 | 70 | - |  | 320 | - | 320XYV42288 | Pair 2 | - | - |  | NON-IS | 320-X -42288 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4201 RECYCLE ISOBUTANE FLUSH TO 320-D-4023 DUMP VESSEL | DOR
Control Valve | 320-UC-42031 |  | - | TYPICAL E2 | R-4201 L6 TO D-4023 | 320-JS-0022 | - | PID-320402301 | - |  | 320-XYV -42302 | - | New |  | DCS | - | 06PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0022 | 70 | - |  | 320 | - | 320XYV42302 | Pair 3 | - | - |  | NON-IS | 320-X -42302 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4201 LOOP REACTOR B LEG .6 TO 320-D-4023 DUMP VESSEL | DOR
Control Valve | 320-UC-42031 |  | - | TYPICAL E2 | R-4201 RIB VENT/D-4023 | 320-JS-0022 | - | PID-320402401 | - |  | 320-XYV -42402 | - | New |  | DCS | - | 06PX2.5MM2/FR/ARM/NIS | - | - | L | 320-CS-0022 | 70 | - |  | 320 | - | 320XYV42402 | Pair 4 | - | - |  | NON-IS | 320-X -42402 | - | Solenoid Valve | XYV | Volt-contact | 320-R-4201 RECYCLE ISOBUTANE VENT TO 320-D-4023 DUMP VESSEL | DOR
General | - |  | - | - | BA-0001 OILY WTR PIT | 500-JE-0013 | - | PID-500000401 | - |  | 500-LI -00032-L | - | New |  | DCS | 4-20 ma | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0013 | 90 | - |  | 500 | - | 500LI00032L | Pair 1 | - | - |  | NON-IS | 500-L -00032 | - | Local Indicator | LI | 2-Wire | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | AO
Level | - |  | - | - | BA-0001 OILY WTR PIT | 500-JE-0013 | - | PID-500000401 | - |  | 500-LT -00032 | - | New |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0013 | 30 | Yes |  | 500 | - | 500LT00032 | Pair 2 | - | - |  | NON-IS | 500-L -00032 | - | Radar Level Transmitter | LT | 2-Wire | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | AI
General | - |  | - | - | BA-0001 OILY WTR PIT | 500-JE-0013 | - | PID-500000401 | - |  | 500-LI -00051-L | - | Modified |  | DCS | 4-20 ma | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0013 | 90 | - |  | 500 | 500-DUMMY-TAG-100 | 500LI00051L | Pair 3 | - | - |  | NON-IS | 500-L -00051 | - | Local Indicator | LI | 2-Wire | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | AO
Level | - |  | - | - | BA-0001 OILY WTR PIT | 500-JE-0013 | - | PID-500000401 | - |  | 500-LT -00051 | - | Modified |  | DCS | 4-20 ma HART | 06PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0013 | 30 | Yes |  | 500 | 500-DUMMY-TAG-304 | 500LT00051 | Pair 4 | - | - |  | NON-IS | 500-L -00051 | - | Radar Level Transmitter | LT | 2-Wire | 500-BA-0001 OILY WATER HOLDING PIT LEVEL | AI
General | 500-UC-00030 |  | - | - | GRND CONN | 500-JE-0015 | - | PID-500000301 | - |  | 500-XS -00322 | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0015 | 34 | - |  | 500 | - | 500XS00322 | Pair 1 | - | NC |  | NON-IS | 500-X -00322 | - | Switch | XS | Voltfree-contact | EARTHING CONNECTION | DIR
General | 500-UC-00060 |  | - | - | GRND CONN | 500-JE-0015 | - | PID-500000601 | - |  | 500-XS -00612 | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0015 | 34 | - |  | 500 | - | 500XS00612 | Pair 2 | - | NC |  | NON-IS | 500-X -00612 | - | Switch | XS | Voltfree-contact | EARTHING CONNECTION | DIR
General | 500-UC-00070 |  | - | - | GRND CONN | 500-JE-0015 | - | PID-500000701 | - |  | 500-XS -00711 | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0015 | 34 | - |  | 500 | - | 500XS00711 | Pair 3 | - | NC |  | NON-IS | 500-X -00711 | - | Switch | XS | Voltfree-contact | EARTHING CONNECTION | DIR
Pressure | - |  | - | - | ZTUA-0004 CAU TO G-0004 | 500-JE-0015 | - | PID-500000601 | - |  | 500-PDT -00611 | - | Modified |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0015 | 30 | Yes |  | 500 | 500-DUMMY-TAG-71 | 500PDT00611 | Pair 4 | - | - |  | NON-IS | 500-PD-00611 | - | Diff. Pressure Transmitter with Seal | PDT | 2-Wire | ZTUA-0004 CAUSTIC SODA UNLOADING TO G-0004 | AI
Pressure | - |  | - | - | ZTUA-0006 HXE TO G-0005 | 500-JE-0015 | - | PID-500000701 | - |  | 500-PDT -00712 | - | Modified |  | DCS | 4-20 ma HART | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | L | 500-CE-0015 | 30 | Yes |  | 500 | 500-DUMMY-TAG-72 | 500PDT00712 | Pair 5 | - | - |  | NON-IS | 500-PD-00712 | - | Diff. Pressure Transmitter with Seal | PDT | 2-Wire | ZTUA-0006 HEXENE-1 TO G-0005 | AI
General | - |  | - | - | IBT TO BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 500-FI -00051-L | - | Modified |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 2 | - |  | 500 | - | 500FI00051L | Pair 1 | - | - |  | NON-IS | 500-F -00051 | - | Local Panel Indicator | FI | 2-Wire | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | ZTUA-0002 IBT UNLD/G-001 | 500-LP-0003 | - | PID-500000301 | - |  | 500-FI -00311-L | - | Modified |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 2 | - |  | 500 | - | 500FI00311L | Pair 2 | - | - |  | NON-IS | 500-F -00311 | - | Local Panel Indicator | FI | 2-Wire | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | AO
General | - |  | - | - | ZTUA-0002 IBT UNLD/G-001 | 500-LP-0003 | - | PID-500000301 | - |  | 500-PI -00313-L | - | Modified |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 40 | - |  | 500 | - | 500PI00313L | Pair 3 | - | - |  | NON-IS | 500-P -00313 | - | Local Panel Indicator | PI | 2-Wire | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | AO
General | 500-UC-00030 |  | - | - | UNLD START | 500-LP-0003 | - | PID-500000301 | - |  | 500-HS -00053-L | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 83 | - |  | 500 | - | 500HS00053L | Pair 4 | - | NO |  | NON-IS | 500-H -00053 | - | Hand Switch | HS | Voltfree-contact | UNLOADING START | DIR
General | 500-UC-00030 |  | - | - | UNLD STOP | 500-LP-0003 | - | PID-500000301 | - |  | 500-HS -00054-L | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 83 | - |  | 500 | - | 500HS00054L | Pair 5 | - | NC |  | NON-IS | 500-H -00054 | - | Hand Switch | HS | Voltfree-contact | UNLOADING STOP | DIR
General | 500-UC-00030 |  | - | - | LOCAL PERM FOR UNLD | 500-LP-0003 | - | PID-500000301 | - |  | 500-HS -00068-L | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 83 | - |  | 500 | - | 500HS00068L | Pair 6 | - | NO |  | NON-IS | 500-H -00068 | - | Hand Switch | HS | Voltfree-contact | LOCAL OPERATOR PERMISSIVE FOR UNLOADING | DIR
General | - |  | - | - | HDR LPN TO FLR | 500-LP-0003 | - | PID-500000301 | - |  | 500-PI -00321-L | - | New |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 500 | - | 500PI00321L | Pair 7 | - | - |  | NON-IS | 500-P -00321 | - | Local Panel Indicator | PI | 2-Wire | HEADER LOW PRESSURE NITROGEN TO FLARE | AO
General | - |  | - | - | IBT TO BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 500-QI -00051-L | - | Modified |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 500 | 500-FQI -00051-L | 500QI00051L | Pair 8 | - | - |  | NON-IS | 500-F -00051 | - | Local Panel Indicator | QI | 2-Wire | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | IBT TO BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 500-TI -00002-L | - | New |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 500 | - | 500TI00002L | Pair 11 | - | - |  | NON-IS | 500-T -00002 | - | Local Panel Indicator | TI | 2-Wire | ISOBUTANE TO ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | IBT BULLET VOL INCREASE | 500-LP-0003 | - | PID-500000301 | - |  | 440-QI -20044-L | - | Modified |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 440 | 440-FQI -20044-L | 440QI20044L | Pair 12 | - | - |  | NON-IS | 440-F -20044 | - | Local Panel Indicator | QI | 2-Wire | ISOBUTANE BULLET VOLUME INCREASE | AO
General | - |  | - | - | IBT BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 440-TI -20044-L | - | New |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 440 | - | 440TI20044L | Pair 13 | - | - |  | NON-IS | 440-T -20044 | - | Local Panel Indicator | TI | 2-Wire | ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | IBT BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 440-PI -20077-L | - | New |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 440 | - | 440PI20077L | Pair 14 | - | - |  | NON-IS | 440-P -20077 | - | Local Panel Indicator | PI | 2-Wire | ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | IBT BULLET 440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 440-LI -20044-L | - | New |  | DCS | 4-20 ma | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A |  | - |  | 440 | - | 440LI20044L | Pair 15 | - | - |  | NON-IS | 440-L -20044 | - | Local Panel Indicator | LI | 2-Wire | ISOBUTANE BULLET 440-D-2014 | AO
General | - |  | - | - | LP#3 LAMP TEST | 500-LP-0003 | - | PID-500000301 | - |  | 500-HS -00351-L | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 83 | - |  | 500 | 500-DUMMY-TAG-75 | 500HS00351L | Pair 16 | - | NO |  | NON-IS | 500-H -00351 | - | Local Panel Hand Switch | HS | Voltfree-contact | LP#3 LAMP TEST | DIR
General | - | ISOBUTANE UNLOADING PUMP | - | - | G-0001 MOT REM INDIC | 500-LP-0003 | - | PID-500000301 | 500-G-0001 |  | 500-MHL -G0001-RL | - | Modified |  | DCS | - | 24PX1MM2/FR/IND&OS/ARM/NIS | - | - | LP | 500-CE-LP-0003-A | 25 | - |  | 500 | 500-DUMMY-TAG-706 | 500MHLG0001RL | Pair 19 | PKG-019003 | - |  | NON-IS | 500-M -G0001 | - | Motor Local / Remote Indication | MHL | Volt-contact | 500-G-0001 MOT REMOTE INDIC | DO
General | 500-UC-00030 |  | - | - | GRND CONN | 500-LP-0003 | - | PID-500000301 | - |  | 500-XA -00322-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 34 | - |  | 500 | - | 500XA00322L | Pair 1 | - | - |  | NON-IS | 500-X -00322 | - | Alarm | XA | Volt-contact | EARTHING CONNECTION | DO
General | 500-UC-00030 |  | - | - | IBT ARM PARKING | 500-LP-0003 | - | PID-500000301 | - |  | 500-XA -00323-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 34 | - |  | 500 | - | 500XA00323L | Pair 2 | - | - |  | NON-IS | 500-X -00323 | - | Alarm | XA | Volt-contact | ISOBUTANE ARM PARKING POSITION | DO
General | 500-UC-00030 |  | - | - | IBT ARM COUPLING | 500-LP-0003 | - | PID-500000301 | - |  | 500-XA -00324-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 34 | - |  | 500 | - | 500XA00324L | Pair 3 | - | - |  | NON-IS | 500-X -00324 | - | Alarm | XA | Volt-contact | ISOBUTANE ARM COUPLING | DO
General | - | ISOBUTANE UNLOADING PUMP | - | - | G-0001 MOT RUNNING INDIC | 500-LP-0003 | - | PID-500000301 | 500-G-0001 |  | 500-MXL -G0001-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 500 | 500-DUMMY-TAG-91 | 500MXLG0001L | Pair 5 | PKG-019003 | - |  | NON-IS | 500-M -G0001 | - | Motor Running Indication | MXL | Volt-contact | 500-G-0001 MOT RUNNING INDIC | DO
General | - |  | - | - | DISCR FQI-00051FQI-00XXX | 500-LP-0003 | - | PID-500000301 | - |  | 500-QAX -00051-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 500 | 500-FQAX -00051-L | 500QAX00051L | Pair 6 | - | - |  | NON-IS | 500-F -00051 | - | Discrepancy Alarm | QAX | Volt-contact | DISCREPANCY BETWEEN 500-FQI-00051 and 440-FQI-00XXX | DO
General | - |  | - | - | ZTUA-0002 IBT UNLD/G-001 | 500-LP-0003 | - | PID-500000301 | - |  | 500-ZLO -00311-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 500 | 500-DUMMY-TAG-99 | 500ZLO00311L | Pair 8 | - | - | - | NON-IS | 500-Z -00311 | - | Position Indication Open | ZLO | Volt-contact | ZTUA-0002 ISOBUTANE UNLOADING TO G-0001 | DO
General | - |  | - | - | UNLD BAY IBT/440-D-2014 | 500-LP-0003 | - | PID-500000301 | - |  | 500-ZLO -00052-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 500 | 500-DUMMY-TAG-98 | 500ZLO00052L | Pair 10 | - | - | - | NON-IS | 500-Z -00052 | - | Position Indication Open | ZLO | Volt-contact | UNLOADING BAY ISOBUTANE TO 440-D-2014 | DO
General | - |  | - | - | 440-ZV-20057 OPN INDIC | 500-LP-0003 | - | PID-500000301 | - |  | 440-ZLO -20057-L | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 440 | - | 440ZLO20057L | Pair 12 | - | - | - | NON-IS | 440-Z -20057 | - | Position Indication Open | ZLO | Volt-contact | 440-ZV-20057 OPEN POSITION INDICATION | DO
General | - |  | - | - | 440-ZV-20027 OPN INDIC | 500-LP-0003 | - | PID-500000301 | - |  | 440-ZLO -20027-L | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 440 | - | 440ZLO20027L | Pair 14 | - | - | - | NON-IS | 440-Z -20027 | - | Position Indication Open | ZLO | Volt-contact | 440-ZV-20027 OPEN POSITION INDICATION | DO
General | - |  | - | - | DCS OPR PERM | 500-LP-0003 | - | PID-500000301 | - |  | 500-XA -00331-L | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 34 | - |  | 500 | - | 500XA00331L | Pair 15 | - | - |  | NON-IS | 500-X -00331 | - | Alarm | XA | Volt-contact | DCS OPERATOR PERMISSIVE | DO
General | - | ISOBUTANE UNLOADING PUMP | - | - | G-0001 MOT FAULT INDIC | 500-LP-0003 | - | PID-500000301 | 500-G-0001 |  | 500-MXA -G0001-L | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B |  | - |  | 500 | 500-DUMMY-TAG-90 | 500MXAG0001L | Pair 16 | PKG-019003 | - |  | NON-IS | 500-M -G0001 | - | Motor Fault Alarm | MXA | Volt-contact | 500-G-0001 MOT FAULT INDIC | DO
General | - | ISOBUTANE UNLOADING PUMP | - | - | G-0001 MOT LOC INDIC | 500-LP-0003 | - | PID-500000301 | 500-G-0001 |  | 500-MHL -G0001-LL | - | Modified |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 24 | - |  | 500 | 500-MHL -G0001-L | 500MHLG0001LL | Pair 17 | PKG-019003 | - |  | NON-IS | 500-M -G0001 | - | Motor Local / Remote Indication | MHL | Volt-contact | 500-G-0001 MOT LOCAL INDIC | DO
General | 500-UC-00030 |  | - | - | N2 ARM PARKING | 500-LP-0003 | - | PID-500000301 | - |  | 500-XA -00341-L | - | New |  | DCS | - | 24PX2.5MM2/FR/ARM/NIS | - | - | LP | 500-CE-LP-0003-B | 34 | - |  | 500 | 500-DUMMY-TAG-703 | 500XA00341L | Pair 18 | - | - |  | NON-IS | 500-X -00341 | - | Alarm | XA | Volt-contact | NITROGEN ARM PARKING POSITION | DO
General | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | LH OS HVAC COM FAIL | OS02-CP-01 | DO | - | 500-OS-02 |  | 500-EJA -00011-D | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 |  | - |  | 500 | - | 500EJA00011D | Pair 1 | - | NC |  | NON-IS | 500-E -00011-D | - | Ventilation Failure | EJA | Voltfree-contact | LIQUID HANDLING OPERATOR SHELTER HVAC COMMON FAILURE | DI
General | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | LH OS HVAC PWR LOSS | OS02-CP-01 | DO | - | 500-OS-02 |  | 500-EJA -00024 | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 |  | - |  | 500 | - | 500EJA00024 | Pair 2 | - | NC |  | NON-IS | 500-E -00024 | - | Power failure switch | EJA | Voltfree-contact | LIQUID HANDLING OPERATOR SHELTER HVAC POWER LOSS ALARM | DI
Temperature | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | LH OS VFD HVAC DUCT | OS02-CP-01 | AO | - | 500-OS-02 |  | 500-TT -00034 | - | New |  | DCS | 4-20 ma | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 |  | No |  | 500 | - | 500TT00034 | Pair 3 | - | - | - | NON-IS | 500-T -00034 | - | Temperature Transmitter | TT | 4-Wire | LIQUID HANDLING OPERATOR SHELTER HVAC RETURN DUCT TEMPERATURE INDICATION | AI
General | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | LH OS HVAC | OS02-CP-01 | DO | - | 500-OS-02 |  | 500-TAQ -00009-D | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 |  | - |  | 500 |  | 500TAQ00009D | Pair 4 | - | NC |  | NON-IS | 500-T -00009-D | - | Cumulative Temperature Alarm | TAQ | Voltfree-contact | LIQUID HANDLING OPERATOR SHELTER AREA HVAC CUMULATIVE TEMPERATURE ALARM | DI
General | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | WH HVAC RUN | OS02-CP-01 | DO | - | 500-OS-02 |  | 500-EJR -00012-D | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 |  | - |  | 500 | - | 500EJR00012D | Pair 5 | - | NC |  | NON-IS | 500-E -00012-D | - | Running Status | EJR | Voltfree-contact | LIQUID HANDLING OPERATOR SHELTER HVAC RUNNING STATUS | DI
General | - | LIQUID HANDLING OPERATOR SHELTER | HVAC | - | LH OS DMP CLS FB | OS02-CP-01 | DO | - | 500-OS-02 |  | 500-DXLS -00003-C | - | New |  | DCS | - | 12PX1MM2/FR/IND&OS/ARM/NIS | - | - | 500-OS-02 | OS02-ICE-6001 | 30 | - |  | 500 | - | 500DXLS00003C | Pair 6 | - | NC |  | NON-IS | 500-DX-00003 | - | Cumulative Damper Close Position Feedback | DXLS | Voltfree-contact | LIQUID HANDLING OPERATOR SHELTER HVAC CUMULATIVE DAMPER CLOSE POSITION FEEDBACK | DI
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-01 TEMPERATURE | - | - | - | P30-DCM-32001-01 | - | 320-EJA -01001-T | - | New | - | DCS | RTD | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01001T | - | - | - | - | NON-IS | 320-E -01001 | - | Cabinet Diagnostic Alarm | EJA | 3-Wire | P30-DCM-32001-01 TEMPERATURE | AIR
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-01 230VAC FAIL | - | - | - | P30-DCM-32001-01 | - | 320-EJA -01001-AC | - | New | - | DCS | - | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01001AC | - | - | NC | - | NON-IS | 320-E -01001 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCM-32001-01 230VAC FAIL | DIR
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-01 24VDC FAIL | - | - | - | P30-DCM-32001-01 | - | 320-EJA -01001-DC | - | New | - | DCS | - | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01001DC | - | - | NC | - | NON-IS | 320-E -01001 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCM-32001-01 24VDC FAIL | DIR
General | - | DCS System Cabinet | - | - | P30-DCS-32001-01 TEMPERATURE | - | - | - | P30-DCS-32001-01 | - | 320-EJA -01031-T | - | New | - | DCS | RTD | 1TX1.3MM2/FR/OS/NIS | - | - | PIB-30 | P30-ICE-0001 | - | - | - | 320 | - | 320EJA01031T | Triad 1 | - | - | - | NON-IS | 320-E -01031 | - | Cabinet Diagnostic Alarm | EJA | 3-Wire | P30-DCS-32001-01 TEMPERATURE | AIR
General | - | DCS System Cabinet | - | - | P30-DCS-32001-01 230VAC FAIL | - | - | - | P30-DCS-32001-01 | - | 320-EJA -01031-AC | - | New | - | DCS | - | 2PX1.3MM2/FR/IND&OS/NIS | - | - | PIB-30 | P30-ICE-0002 | - | - | - | 320 | - | 320EJA01031AC | Pair 1 | - | NC | - | NON-IS | 320-E -01031 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCS-32001-01 230VAC FAIL | DIR
General | - | DCS System Cabinet | - | - | P30-DCS-32001-01 24VDC FAIL | - | - | - | P30-DCS-32001-01 | - | 320-EJA -01031-DC | - | New | - | DCS | - | 2PX1.3MM2/FR/IND&OS/NIS | - | - | PIB-30 | P30-ICE-0002 | - | - | - | 320 | - | 320EJA01031DC | Pair 2 | - | NC | - | NON-IS | 320-E -01031 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCS-32001-01 24VDC FAIL | DIR
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-04 TEMPERATURE | - | - | - | P30-DCM-32001-04 | - | 320-EJA -01004-T | - | New | - | DCS | RTD | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01004T | - | - | - | - | NON-IS | 320-E -01004 | - | Cabinet Diagnostic Alarm | EJA | 3-Wire | P30-DCM-32001-04 TEMPERATURE | AIR
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-04 230VAC FAIL | - | - | - | P30-DCM-32001-04 | - | 320-EJA -01004-AC | - | New | - | DCS | - | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01004AC | - | - | NC | - | NON-IS | 320-E -01004 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCM-32001-04 230VAC FAIL | DIR
General | - | DCS Marshalling Cabinet | - | - | P30-DCM-32001-04 24VDC FAIL | - | - | - | P30-DCM-32001-04 | - | 320-EJA -01004-DC | - | New | - | DCS | - | - | - | - | PIB-30 | Internal Wiring | - | - | - | 320 | - | 320EJA01004DC | - | - | NC | - | NON-IS | 320-E -01004 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P30-DCM-32001-04 24VDC FAIL | DIR
General | - | DCS Marshalling Cabinet | - | - | P24-DCM-50002-01 TEMPERATURE | - | - | - | P24-DCM-50002-01 | - | 500-EJA -01021-T | - | New | - | DCS | RTD | - | - | - | PIB-24 | Internal Wiring | - | - | - | 500 | - | 500EJA01021T | - | - | - | - | NON-IS | 500-E -01021 | - | Cabinet Diagnostic Alarm | EJA | 3-Wire | P24-DCM-50002-01 TEMPERATURE | AIR
General | - | DCS Marshalling Cabinet | - | - | P24-DCM-50002-01 230VAC FAIL | - | - | - | P24-DCM-50002-01 | - | 500-EJA -01021-AC | - | New | - | DCS | - | - | - | - | PIB-24 | Internal Wiring | - | - | - | 500 | - | 500EJA01021AC | - | - | NC | - | NON-IS | 500-E -01021 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P24-DCM-50002-01 230VAC FAIL | DIR
General | - | DCS Marshalling Cabinet | - | - | P24-DCM-50002-01 24VDC FAIL | - | - | - | P24-DCM-50002-01 | - | 500-EJA -01021-DC | - | New | - | DCS | - | - | - | - | PIB-24 | Internal Wiring | - | - | - | 500 | - | 500EJA01021DC | - | - | NC | - | NON-IS | 500-E -01021 | - | Cabinet Diagnostic Alarm | EJA | Voltfree-contact | P24-DCM-50002-01 24VDC FAIL | DIR